## Overview
TRIBE DIGITAL BOILER MODEL
Economic model for modular data centre heat recovery
Version 3.1 - Dynamic Capex ¦ January 2026
HOW TO USE THIS MODEL
Step 1 | Configure Hardware | Go to '0. Rack Profile' and select your chipset (dropdown in B6) and cooling method (dropdown in B17). Optionally adjust the module IT capacity target (B36).
Step 2 | Review Module Specs | Check '1. Module Criteria' to see the resulting module specifications. Enable/disable heat pump (B15) and set output temperature if needed.
Step 3 | Check Capex | Review '2. Module Capex' - costs are calculated automatically from your hardware choices. Adjust Reference Data rates if needed.
Step 4 | Select Customer Process | Go to '5. Buyer Profile' and select an industrial process from the dropdown (B11). The model calculates how many modules are needed.
Step 5 | Review System Economics | Check '6. System Capex' for total investment, '9. System P&L' for revenue and profit analysis.
Step 6 | Adjust Assumptions | Fine-tune costs in '11. Reference Data' (yellow cells). All downstream calculations update automatically.
MODEL STRUCTURE
Sheet | Purpose | Key Features
0. Rack Profile | Hardware config | Chipset, cooling method, rack density, heat capture
1. Module Criteria | Module specs | Heat pump config, thermal output, heat pricing
2. Module Capex | Module capital cost | Dynamic from Rack Profile - enclosure, cooling, power, thermal, monitoring
3. Module Opex | Module operating cost | Electricity, maintenance, insurance
4. Module Flow | Module hydraulics | Flow rates, pipe sizing
5. Buyer Profile | Customer matching | Process selection, modules required, heat balance, rejection sizing
6. System Capex | System capital | Total investment including rejection equipment
7. System Opex | System operating cost | Including rejection running costs
8. System Flow | System hydraulics | Supply vs demand, utilisation, constraints
9. System P&L | Profit & loss | Revenue (compute + heat), costs, margins, payback
11. Reference Data | Lookup tables | Hardware costs, chipset specs, rejection rates, process ΔT
12. Process Library | Process database | 42 industrial heat processes with source citations
KEY CONCEPTS
BYOGPU Model | Customers bring their own GPUs - capex covers infrastructure only, not compute hardware
Thermal vs Flow | Low ΔT processes become flow-constrained, needing more modules than thermal demand alone
Heat Rejection | Equipment sized for 100% rejection (buyer offline); opex based on actual excess
Cooling Premium | DTC +15%, Single-phase immersion +25%, Two-phase +40% vs air-cooled
Dynamic Capex | Module costs auto-calculate from Rack Profile - change chipset/cooling, capex updates
DATA FLOW
Rack Profile → Module Criteria → Module Capex/Opex → Buyer Profile → System Capex/Opex/P&L
INPUT CONVENTIONS
Yellow cells | Example | Adjustable inputs - safe to modify
Blue headers | Example | Section headers - do not edit
White cells | Example | Calculated values - do not edit
KEY INPUTS QUICK REFERENCE
Location | Input | Options
Rack Profile B6 | Chipset | NVIDIA H100/H200/B200, AMD MI300X, Intel Gaudi 3
Rack Profile B17 | Cooling method | DTC, Single-Phase Immersion, Two-Phase Immersion, RDHX
Rack Profile B36 | Module size | IT capacity target in kW (default 250)
Module Criteria B15 | Heat pump | 1 = enabled, 0 = disabled
Module Criteria B29 | Heat price | £/MWh for heat sales
Buyer Profile B11 | Process | Select from dropdown (42 options)
Reference Data B71+ | Hardware costs | All yellow cells - adjust to your pricing

## Agent Context
AGENT CONTEXT
Context and guidelines for AI agents working on this model
BUSINESS CONTEXT
Business Model | TRIBE operates 'digital boilers' - modular data centres co-located on industrial sites that capture waste heat from GPU compute and sell it to industrial partners.
BYOGPU | Customers bring their own GPUs - TRIBE provides infrastructure only. Capex excludes compute hardware costs.
Heat Capture | Liquid cooling (DTC or immersion) captures 75-98% of server waste heat at 45-57°C. Heat pumps lift this to 70-90°C for industrial use.
Revenue Streams | 1) Compute hosting fees (£/kW/month), 2) Heat sales to industrial buyer (£/MWh)
Target Customers | Industrial processes requiring low-grade heat: pasteurisation, CIP systems, district heating, commercial laundry, swimming pools, HVAC
MODEL ARCHITECTURE
Data Flow | Rack Profile → Module Criteria → Module Capex/Opex/Flow → Buyer Profile → System Capex/Opex/Flow/P&L
Rack Profile | INPUTS: Chipset (dropdown B6), Cooling method (dropdown B17), Module IT target (B36). OUTPUTS: Rack density, heat capture rate, capex premium.
Module Criteria | INPUTS: Heat pump toggle (B15), HP output temp (B16), Heat pricing (B27-B29). OUTPUTS: Per-module thermal output, COP.
Module Capex | DYNAMIC CALCULATION from Rack Profile. References costs in '11. Reference Data' rows 71-105. Conditional DTC vs Immersion blocks.
Buyer Profile | INPUT: Process selection dropdown (B11) from Process Library. OUTPUTS: Modules required, binding constraint (thermal vs flow), heat rejection sizing.
System Sheets | Aggregate module-level calculations × number of modules. Add shared infrastructure, rejection equipment, integration costs.
Reference Data | LOOKUP TABLES: Rejection infrastructure (rows 9-16), Cooling characteristics (rows 22-27), Chipsets (rows 33-38), Hardware capex (rows 71-105).
Process Library | DATABASE of 42 industrial processes with temp, thermal load, operating hours, ΔT, source citations. Feeds Buyer Profile dropdown.
KEY TECHNICAL CONCEPTS
Thermal vs Flow Constraint | Low ΔT processes (e.g. pasteurisation, 5°C) become FLOW-constrained - need more modules than thermal demand alone. High ΔT processes (e.g. district heating, 30°C) are THERMAL-constrained.
Heat Pump Thermodynamics | Q_hot = Q_cold × COP/(COP-1). Electrical input = Q_hot/COP. COP decreases with higher temperature lift (source→sink).
Heat Rejection Sizing | CAPEX sized for 100% rejection (worst case - buyer goes offline). OPEX based on ACTUAL excess heat during normal operation.
Cooling Method Trade-offs | DTC: 75% capture, 57.5°C, +15% capex, larger footprint. Immersion: 95-98% capture, 50-55°C, +25-40% capex, denser packing.
Rack Thermal Limits | DTC: 80kW/rack, Single-phase immersion: 100kW/rack, Two-phase: 120kW/rack. Determines GPU density and module footprint.
FORMULA CONVENTIONS
Cross-sheet references | Use full sheet names in quotes, e.g. ='0. Rack Profile'!B37
Conditional blocks | DTC vs Immersion costs use IF(B6="Direct-to-Chip (DTC)",...) pattern
Unit conversions | kWh to MWh: divide by 1000. Annual hours: 8760. Heat: kWth (thermal kilowatts).
Currency | All values in GBP (£). Format: £#,##0 for whole numbers, £#,##0.00 for decimals.
Percentages | Store as decimals (0.15 not 15%), format as 0.0% for display.
KEY CELL REFERENCES
Cell | Description | Notes
0. Rack Profile!B6 | Chipset selection (dropdown) | Drives TDP, density, cost assumptions
0. Rack Profile!B17 | Cooling method selection (dropdown) | Drives heat capture rate, PUE, capex, source ΔT
0. Rack Profile!B23 | PUE by cooling method | From Reference Data lookup. Drives infrastructure power.
0. Rack Profile!B37 | Racks per module | Calculated from space constraints
0. Rack Profile!B40 | Module IT capacity (kW) | TDP × racks per module
0. Rack Profile!B43 | Captured heat (kWth) | IT capacity × heat capture rate
1. Module Criteria!B15 | Heat pump enabled (1/0) | Toggles HP capex/opex calculations
1. Module Criteria!B16 | Heat pump output temp (°C) | Input for COP calculation
1. Module Criteria!B17 | COP (Carnot-based) | 0.5×(T_out+273)/ΔT lift. Dynamic by temps.
1. Module Criteria!B21 | Module thermal output (kWth) | Captured × COP/(COP-1)
4. Module Flow!B11 | Source loop ΔT (°C) | Lookup by cooling method (3-15°C). Was hardcoded 10°C.
4. Module Flow!B21 | Sink loop ΔT (°C) | Fixed 10°C (module design). Process ΔT may differ.
5. Buyer Profile!B11 | Process selection (dropdown) | Drives all demand parameters from Process Library
5. Buyer Profile!B24 | Process ΔT (°C) | From Process Library. Range 5-30°C by process.
5. Buyer Profile!B33 | Modules needed (thermal) | CEIL(demand/module_output)
5. Buyer Profile!B34 | Modules needed (flow) | Reference only - not used in sizing
5. Buyer Profile!B35 | MODULES REQUIRED | B33 (thermal only). Core sizing output.
5. Buyer Profile!B36 | Flow deficit (m³/hr) | MAX(0, buyer_flow - modules×module_flow)
5. Buyer Profile!B37 | Flow ratio | buyer_flow / system_flow. For sizing reference.
5. Buyer Profile!B84 | Augmentation pumps required | ROUNDUP(deficit/25). Discrete equipment count.
5. Buyer Profile!B85 | Actual pump capacity (m³/hr) | pumps × 25 m³/hr standard size
5. Buyer Profile!B86 | Augmented system flow | base_flow + pump_capacity
5. Buyer Profile!B87 | Flow requirement met? | YES/NO verification
6. System Capex!B43 | Plant equipment subtotal | Modules + shared infrastructure
6. System Capex!B44 | Heat rejection subtotal | Dry coolers + controls
6. System Capex!B45 | Hydraulic augmentation subtotal | Pumps + mixing valve + pipe
6. System Capex!B46 | TOTAL SYSTEM CAPEX | plant + rejection + hydraulic
7. System Opex!B37 | TOTAL SYSTEM OPEX | All operating costs incl. hydraulic pumps
9. System P&L!B44 | Annual gross profit | Revenue - opex
11. Reference Data!B71-B105 | Hardware capex rates | Input assumptions for module capex
11. Reference Data!B120-B124 | Hydraulic augmentation rates | Pump £150/m³/hr, valve £2500, pipe £50/m³/hr, std pump 25m³/hr
11. Reference Data!E23-E27 | Source ΔT by cooling method | DTC=10, Single=6, Two=3, RDHX=12, Air=15°C
CURRENT MODEL ARCHITECTURE
Module Sizing Logic | Modules sized on THERMAL capacity only (not flow). Module count = CEIL(heat_demand / module_output).
Flow Handling | Flow deficits handled via hydraulic augmentation (pumps, mixing valves) at ~£8k vs £250k+ per extra module.
ΔT Chain | Cooling Method → Source ΔT (variable) → Source Flow. Module Sink ΔT (fixed 10°C) vs Process ΔT (variable) → Flow Deficit → Hydraulics.
COP Calculation | Carnot-based: COP = 0.5 × (T_out + 273) / (T_out - T_source). Dynamic based on actual temperatures.
Infrastructure Power | Derived from PUE by cooling method (PUE - 1). Not hardcoded.
KEY DESIGN DECISIONS
Decision | Rationale
Thermal-only module sizing | Physics: Q=ṁ×Cp×ΔT means sufficient heat can always match flow via blending. Flow is hydraulic cost, not module constraint.
Fixed module sink ΔT (10°C) | Standard module design. Process ΔT varies (5-30°C). Mismatch creates flow deficit handled by augmentation.
Variable source ΔT by cooling | Two-phase immersion has lower ΔT (3°C) vs air cooling (15°C). Affects source-side flow and pump sizing.
Discrete pump sizing (25 m³/hr) | Standard commercial pump size. Count = ROUNDUP(deficit/25). Provides clear BOM and capex.
COP varies with temperature | Real HP performance. Higher lift = lower COP = more electricity. Carnot efficiency ~50% typical.
CHANGE LOG (January 2026)
Change | Impact
COP: Hardcoded 4 → Carnot formula | COP now 3-6 depending on temps. Affects HP electricity and thermal output.
Module sizing: MAX(thermal,flow) → thermal only | Pasteurisation: 5 modules → 3 modules (-40% capex). Flow deficit via pumps.
Infrastructure power: 5% → PUE-based | DTC: 2% overhead. Immersion: 5-40%. Reflects actual cooling method efficiency.
Source ΔT: Hardcoded 10°C → cooling method lookup | Two-phase: 3°C. Air: 15°C. Affects source flow calculations.
Added hydraulic augmentation | New capex/opex sections for pumps, mixing valves when flow deficit exists.
Added discrete pump sizing | Pump count, capacity, verification. Flows through BOM and capex.
Fixed broken references | Module Opex maintenance/insurance, Buyer Profile heat balance, System P&L profit formulas.
Added formula documentation (F/G/H columns) | All calculation sheets now have Intent, Explanation, and Dependents columns.
DOCUMENTATION STRUCTURE
Column F: Intent | Why this cell exists - business/engineering purpose
Column G: Explanation | What the formula/value does technically
Column H: Dependents | Cells that directly reference this cell
Purpose
Formula documentation | Every calculation sheet (0-11) has columns F and G for documentation. This enables traceability and reduces errors during model updates.
Dependency tracking | Direct dependents only (not cascading). Shows which downstream calculations would be affected if this cell changes.
Maintenance Guidelines
When adding a new formula | Add explanation in column F describing the formula's purpose. Check if any cells reference this new cell and update their Dependents.
When modifying a formula | Update the explanation if the logic changes. Review dependents to ensure downstream calculations still make sense.
When deleting a cell | Check Dependents column first. If any cells reference this one, update or remove those formulas before deleting.
Format Conventions
Intent column | Brief statement of purpose (5-15 words). Focus on WHY not WHAT.
Explanation column | Technical description of formula logic or value source.
Dependents column | Format: Sheet!Cell - Description. Max 10 entries shown.

## 0. Rack Profile
RACK PROFILE |  |  |  |  | Intent | Explanation | Dependents
Define module hardware configuration - chipset and cooling approach |  |  |  |  | Define GPU hardware to determine power and cooling requirements | Row label only
CHIPSET CONFIGURATION
Chipset type | NVIDIA H100 |  |  |  | Define GPU hardware to determine power and cooling requirements | Text value for Chipset type | 0. Rack Profile!B9 - TDP per chip (W); 0. Rack Profile!B10 - Chips per server; 0. Rack Profile!B12 - Max junction temp (°C); 2. Module Capex!B5 - Chipset; 5. Buyer Profile!B5 - Chipset; 6. System Capex!B5 - Chipset; 7. System Opex!B5 - Chipset; 8. System Flow!B5 - Chipset; 9. System P&L!B8 - Chipset
Chipset Specifications |  |  |  |  | Define GPU hardware to determine power and cooling requirements | Row label only
TDP per chip (W) |  | Thermal Design Power |  |  | Establish base power draw for thermal calculations | Conditional logic for TDP per chip (W) | 0. Rack Profile!B11 - Server power (kW)
Chips per server |  | Typical GPU count per node |  |  | Configure server density for rack power calculations | Conditional logic for Chips per server | 0. Rack Profile!B11 - Server power (kW); 0. Rack Profile!B30 - GPUs per rack
Server power (kW) |  | Chip TDP × count × 1.15 (overhead) |  |  | Calculate total server power including overhead for sizing | Calculated from upstream values for Server power (kW) | 0. Rack Profile!B29 - Servers per rack; 0. Rack Profile!B31 - Actual rack power (kW)
Max junction temp (°C) |  | Chip thermal limit |  |  | Define thermal limits to ensure safe GPU operation | Conditional logic for Max junction temp (°C) | 0. Rack Profile!B13 - Recommended coolant inlet (°C)
Recommended coolant inlet (°C) |  | Target 25°C below Tj max |  |  | Set cooling system design temperature | Calculated from upstream values for Recommended coolant inlet (°C)
COOLING APPROACH
Cooling method | Direct-to-Chip (DTC) |  |  |  | Select cooling technology to determine heat capture and costs | Text value for Cooling method | 0. Rack Profile!B20 - Heat capture rate (%); 0. Rack Profile!B21 - Capture temperature (°C); 0. Rack Profile!B22 - Coolant type; 0. Rack Profile!B23 - PUE contribution; 0. Rack Profile!B24 - Capex premium vs air-cooled (%); 0. Rack Profile!B25 - Rack thermal limit (kW/rack); 2. Module Capex!B6 - Cooling method; 4. Module Flow!B11 - Source loop ΔT (°C); 5. Buyer Profile!B6 - Cooling method; 6. System Capex!B6 - Cooling method; ... and 3 more
Cooling Method Characteristics |  |  |  |  | Select cooling technology to determine heat capture and costs | Row label only
Heat capture rate (%) |  | Fraction of IT heat captured to liquid |  |  | Quantify recoverable heat for revenue calculations | Conditional logic for Heat capture rate (%) | 0. Rack Profile!B43 - Captured heat (kWth); 0. Rack Profile!B45 - Residual heat to air (kWth); 0. Rack Profile!B63 - Total heat output (per kW IT); 1. Module Criteria!B10 - Heat capture rate (%)
Capture temperature (°C) |  | Typical coolant outlet temperature |  |  | Determine heat quality for buyer matching | Conditional logic for Capture temperature (°C) | 0. Rack Profile!B44 - Capture temperature (°C); 0. Rack Profile!B49 - Heat capture quality; 0. Rack Profile!B50 - Heat pump requirement; 0. Rack Profile!B51 - Recommended HP output (°C); 0. Rack Profile!B52 - Estimated COP at recommended output; 0. Rack Profile!B60 - Temperature lift (K); 1. Module Criteria!B12 - Capture temperature (°C); 8. System Flow!B7 - Capture temperature (°C)
Coolant type |  |  |  |  | Specify fluid for equipment selection | Conditional logic for Coolant type
PUE contribution |  | Cooling system efficiency factor |  |  | Model infrastructure efficiency for opex calculations | Conditional logic for PUE contribution | 3. Module Opex!B6 - Infrastructure power (from PUE)
Capex premium vs air-cooled (%) |  |  |  |  | Account for cooling technology cost differences | Conditional logic for Capex premium vs air-cooled (%) | 2. Module Capex!B59 - Premium rate (%)
Rack thermal limit (kW/rack) |  | Max power per 42U rack |  |  | Set rack density constraint for module sizing | Conditional logic for Rack thermal limit (kW/rack) | 0. Rack Profile!B29 - Servers per rack; 0. Rack Profile!B32 - Rack thermal utilisation (%)
RACK CONFIGURATION
Servers per rack |  | Rack thermal limit ÷ server power |  |  | Calculate achievable density within thermal limits | Rounded calculation for Servers per rack | 0. Rack Profile!B30 - GPUs per rack; 0. Rack Profile!B31 - Actual rack power (kW); 0. Rack Profile!B38 - Servers per module
GPUs per rack |  | Servers per rack × chips per server |  |  | Compute total GPU capacity per rack | Calculated from upstream values for GPUs per rack | 0. Rack Profile!B39 - GPUs per module
Actual rack power (kW) |  | May be less than thermal limit |  |  | Determine actual power for infrastructure sizing | Calculated from upstream values for Actual rack power (kW) | 0. Rack Profile!B32 - Rack thermal utilisation (%); 0. Rack Profile!B37 - Racks per module; 0. Rack Profile!B40 - Actual module IT capacity (kW)
Rack thermal utilisation (%) |  | Actual vs limit |  |  | Assess how well rack capacity is used | Calculated from upstream values for Rack thermal utilisation (%)
MODULE SUMMARY
Module IT capacity target (kW) | 250 | Design target - adjust as needed |  |  | Define standardised module size for business model | Input parameter: Module IT capacity target (kW) | 0. Rack Profile!B37 - Racks per module
Racks per module |  | To meet capacity target |  |  | Calculate rack count to meet module capacity target | Rounded calculation for Racks per module | 0. Rack Profile!B38 - Servers per module; 0. Rack Profile!B39 - GPUs per module; 0. Rack Profile!B40 - Actual module IT capacity (kW); 2. Module Capex!B7 - Racks per module
Servers per module |  |  |  |  | Aggregate compute capacity at module level | Calculated from upstream values for Servers per module | 2. Module Capex!B8 - Servers per module
GPUs per module |  |  |  |  | Aggregate compute capacity at module level | Calculated from upstream values for GPUs per module | 2. Module Capex!B69 - Capex per GPU (£/GPU); 5. Buyer Profile!B7 - GPUs per module; 6. System Capex!B7 - GPUs per module; 7. System Opex!B7 - GPUs per module
Actual module IT capacity (kW) |  | May differ slightly from target |  |  | Define standardised module size for business model | Calculated from upstream values for Actual module IT capacity (kW) | 0. Rack Profile!B43 - Captured heat (kWth); 0. Rack Profile!B45 - Residual heat to air (kWth); 0. Rack Profile!B68 - Heat delivered (MWh/yr); 1. Module Criteria!B5 - Module IT capacity (kW); 2. Module Capex!B9 - Module IT capacity (kW); 5. Buyer Profile!B8 - Module IT capacity (kW); 6. System Capex!B48 - Capex per IT kW (£/kW)
Heat Output |  |  |  |  | Calculate annual heat sales volume
Captured heat (kWth) |  | Available for heat recovery |  |  | Calculate heat available for sale to buyers | Calculated from upstream values for Captured heat (kWth) | 0. Rack Profile!B69 - HP electricity (MWh/yr); 2. Module Capex!B10 - Captured heat (kWth)
Capture temperature (°C) |  |  |  |  | Determine heat quality for buyer matching | Formula: Capture temperature (°C)
Residual heat to air (kWth) |  | Requires conventional cooling |  |  | Identify heat requiring rejection (cost) | Calculated from upstream values for Residual heat to air (kWth)
HEAT RECOVERY ASSESSMENT
Heat capture quality |  |  |  |  | Classify heat grade for buyer matching | Conditional logic for Heat capture quality
Heat pump requirement |  |  |  |  | Determine if temperature boost needed for applications | Conditional logic for Heat pump requirement | 0. Rack Profile!B52 - Estimated COP at recommended output
Recommended HP output (°C) |  |  |  |  | Model parameter | Conditional logic for Recommended HP output (°C) | 0. Rack Profile!B52 - Estimated COP at recommended output; 0. Rack Profile!B57 - Target output temperature (°C)
Estimated COP at recommended output |  | Carnot-based estimate |  |  | Calculate heat pump efficiency for economics | Conditional logic for Estimated COP at recommended output
HEAT PUMP ECONOMICS
Trade-off analysis: capture efficiency vs. HP operating cost |  |  |  |  | Financial input or calculation | Row label only
Target output temperature (°C) |  | From heat recovery assessment |  |  | Temperature parameter for thermal design | Formula: Target output temperature (°C) | 0. Rack Profile!B60 - Temperature lift (K); 0. Rack Profile!B61 - COP at this lift
Electricity price (£/kWh) | 0.18 | Grid electricity rate |  |  | Financial input or calculation | Input parameter: Electricity price (£/kWh) | 0. Rack Profile!B64 - HP electricity cost (£/kWth·hr); 0. Rack Profile!B70 - HP electricity cost (£/yr)
Temperature lift (K) |  | Output temp - capture temp |  |  | Define upgrade required from source to delivery temp | Calculated from upstream values for Temperature lift (K) | 0. Rack Profile!B61 - COP at this lift
COP at this lift |  | Carnot-based estimate |  |  | Calculate heat pump efficiency for economics | Conditional logic for COP at this lift | 0. Rack Profile!B62 - HP electricity per kWth captured; 0. Rack Profile!B63 - Total heat output (per kW IT)
HP electricity per kWth captured |  | kWh elec per kWh heat lifted |  |  | Model heat pump operating cost | Conditional logic for HP electricity per kWth captured | 0. Rack Profile!B64 - HP electricity cost (£/kWth·hr); 0. Rack Profile!B69 - HP electricity (MWh/yr)
Total heat output (per kW IT) |  | Captured × COP/(COP-1) |  |  | Calculate annual heat sales volume | Conditional logic for Total heat output (per kW IT) | 0. Rack Profile!B68 - Heat delivered (MWh/yr)
HP electricity cost (£/kWth·hr) |  | Marginal cost to deliver heat |  |  | Model heat pump operating cost | Conditional logic for HP electricity cost (£/kWth·hr)
Module Annual Analysis |  |  |  |  | Model parameter | Row label only
Annual operating hours | 8000 | Typical utilisation |  |  | Model parameter | Input assumption: Annual operating hours | 0. Rack Profile!B68 - Heat delivered (MWh/yr); 0. Rack Profile!B69 - HP electricity (MWh/yr)
Heat delivered (MWh/yr) |  | Per module |  |  | Calculate annual heat sales volume | Conditional logic for Heat delivered (MWh/yr)
HP electricity (MWh/yr) |  | Per module |  |  | Model heat pump operating cost | Conditional logic for HP electricity (MWh/yr) | 0. Rack Profile!B70 - HP electricity cost (£/yr)
HP electricity cost (£/yr) |  | Per module |  |  | Model heat pump operating cost | Calculated from upstream values for HP electricity cost (£/yr)
COOLING METHOD COMPARISON
Method | Capture % | Temp °C | Lift to 90°C | COP | Model parameter | Text value for Method | Heat out/kW IT
Direct-to-Chip (DTC) | 75% | 57.5 | 32.5K | 4.4 | Model parameter | Text value for Direct-to-Chip (DTC) | 97%
Single-Phase Immersion | 95% | 50 | 40K | 3.8 | Model parameter | Text value for Single-Phase Immersion | 128%
Two-Phase Immersion | 98% | 55 | 35K | 4.2 | Model parameter | Text value for Two-Phase Immersion | 128%
Rear Door Heat Exchanger | 50% | 45 | 45K | 3.4 | Model parameter | Text value for Rear Door Heat Exchanger | 70%
KEY INSIGHT: | [5 empty] | Row label only
Immersion captures more heat but requires more HP electricity due to lower capture temperature. |  |  |  |  | Determine heat quality for buyer matching | Row label only
DTC offers the best balance of capture efficiency and HP operating cost for high-temp applications. |  |  |  |  | Financial input or calculation | Row label only

## 1. Module Criteria
MODULE CRITERIA |  |  |  | Intent | Explanation | Dependents
Hardware specifications and configuration for a single digital boiler module |  |  |  | Model parameter | Row label only
COMPUTE SPECIFICATIONS
Module IT capacity (kW) |  | From Rack Profile (actual) | Standard MDC module size | Pull standardised module size for consistent sizing | Pulls value from 0. Rack Profile!B40 | 1. Module Criteria!B11 - Captured heat (kWth); 3. Module Opex!B7 - Infrastructure power cost (£/yr); 5. Buyer Profile!B65 - Total IT capacity (kW); 9. System P&L!B12 - Module IT capacity (kW)
Compute rate (£/kW/month) | 150 |  | Colocation pricing | Financial input or calculation | Input parameter: Compute rate (£/kW/month) | 9. System P&L!B13 - Rack rate (£/kW/month)
Target utilisation rate (%) | 90% |  | Steady-state capacity utilisation | Model realistic capacity usage for revenue | Input parameter: Target utilisation rate (%) | 1. Module Criteria!B24 - Annual heat output (MWh); 3. Module Opex!B7 - Infrastructure power cost (£/yr); 3. Module Opex!B9 - Heat pump electricity (£/yr); 5. Buyer Profile!B92 - Cooling infrastructure (kW); 9. System P&L!B15 - Utilisation assumption (%)
HEAT CAPTURE SPECIFICATIONS
Heat capture rate (%) |  | From Rack Profile (cooling method) | % of IT load captured via DTC cooling | Reference thermal specifications from rack design | Pulls value from 0. Rack Profile!B20 | 1. Module Criteria!B11 - Captured heat (kWth)
Captured heat (kWth) |  |  | Thermal output without heat pump | Power or thermal capacity metric | Calculated from upstream values for Captured heat (kWth) | 1. Module Criteria!B18 - Heat pump capacity (kWth); 1. Module Criteria!B21 - Thermal output (kWth); 4. Module Flow!B9 - Thermal power (kWth)
Capture temperature (°C) |  | From Rack Profile (cooling method) | DTC cooling loop output temperature | Temperature parameter for thermal design | Pulls value from 0. Rack Profile!B21 | 1. Module Criteria!B17 - Heat pump COP; 1. Module Criteria!B22 - Delivery temperature (°C); 4. Module Flow!B10 - Inlet temperature (°C); 5. Buyer Profile!B69 - Heat pump required?; 5. Buyer Profile!B70 - Temperature lift required (K)
HEAT PUMP CONFIGURATION
Heat pump enabled? | 1 |  | 1 = Yes, 0 = No | Toggle heat pump for scenario analysis | Flag enabled for Heat pump enabled? | 1. Module Criteria!B17 - Heat pump COP; 1. Module Criteria!B21 - Thermal output (kWth); 1. Module Criteria!B22 - Delivery temperature (°C); 1. Module Criteria!B29 - Effective heat price (£/MWh); 2. Module Capex!B53 - Heat pump unit; 2. Module Capex!B54 - Heat pump installation; 2. Module Capex!B55 - Heat pump controls; 3. Module Opex!B9 - Heat pump electricity (£/yr); 3. Module Opex!B18 - Heat pump maintenance (£/yr)
Heat pump output temperature (°C) | 90 |  | Delivery temperature to industrial partner | Temperature parameter for thermal design | Input parameter: Heat pump output temperature (°C) | 1. Module Criteria!B17 - Heat pump COP; 1. Module Criteria!B22 - Delivery temperature (°C)
Heat pump COP |  |  | Carnot-based: η × T_hot(K) / ΔT | Calculate heat pump efficiency at operating conditions | Conditional logic for Heat pump COP | 1. Module Criteria!B21 - Thermal output (kWth); 3. Module Opex!B9 - Heat pump electricity (£/yr); 5. Buyer Profile!B73 - HP electrical demand (kW)
Heat pump capacity (kWth) |  |  | Sized to captured heat | Define or calculate system capability | Formula: Heat pump capacity (kWth) | 2. Module Capex!B53 - Heat pump unit; 5. Buyer Profile!B72 - Total HP capacity (kWth)
MODULE OUTPUT SUMMARY
Thermal output (kWth) |  |  | With HP: includes compressor work (COP protected) | Calculate total heat delivery including HP boost | Conditional logic for Thermal output (kWth) | 1. Module Criteria!B24 - Annual heat output (MWh); 3. Module Opex!B9 - Heat pump electricity (£/yr); 4. Module Flow!B19 - Thermal power delivered (kWth); 5. Buyer Profile!B28 - Module thermal capacity (kWth)
Delivery temperature (°C) |  |  |  | Set required output temperature for buyer | Conditional logic for Delivery temperature (°C) | 4. Module Flow!B20 - Outlet temperature (°C); 5. Buyer Profile!B29 - Module delivery temp (°C); 8. System Flow!B20 - Delivery temperature (°C)
Hours per year | 8760 |  | 24/7 operation | Model parameter | Input assumption: Hours per year | 1. Module Criteria!B24 - Annual heat output (MWh); 3. Module Opex!B7 - Infrastructure power cost (£/yr); 3. Module Opex!B9 - Heat pump electricity (£/yr)
Annual heat output (MWh) |  |  |  | Convert to annual volume for revenue calculation | Calculated from upstream values for Annual heat output (MWh)
HEAT PRICING
Base heat price - no HP (£/MWh) | 25 |  | Low-temp heat (55-60°C) | Set heat sales price assumption | Input parameter: Base heat price - no HP (£/MWh) | 1. Module Criteria!B29 - Effective heat price (£/MWh)
Premium heat price - with HP (£/MWh) | 40 |  | High-temp heat (90°C) | Set heat sales price assumption | Input parameter: Premium heat price - with HP (£/MWh) | 1. Module Criteria!B29 - Effective heat price (£/MWh)
Effective heat price (£/MWh) |  |  |  | Set heat sales price assumption | Conditional logic for Effective heat price (£/MWh) | 9. System P&L!B20 - Heat price (£/MWh)
Reference: Industrial gas price (£/MWh) | 53 |  | UK industrial gas benchmark | Financial input or calculation | Input parameter: Reference: Industrial gas price (£/MWh)

## 2. Module Capex
MODULE CAPEX |  |  | Intent | Explanation | Dependents
Capital expenditure for a single digital boiler module | Calculated dynamically from Rack Profile inputs |  | Model parameter | Text value for Capital expenditure for a single digital boiler module
CONFIGURATION SUMMARY
Chipset |  |  | Model parameter | Pulls value from 0. Rack Profile!B6
Cooling method |  |  | Model parameter | Pulls value from 0. Rack Profile!B17 | 2. Module Capex!B19 - Cold plate kits; 2. Module Capex!B20 - CDU (base); 2. Module Capex!B21 - CDU (capacity scaling); 2. Module Capex!B22 - Manifolds & quick-connects; 2. Module Capex!B23 - Primary loop piping; 2. Module Capex!B27 - Immersion tanks; 2. Module Capex!B28 - Dielectric fluid (initial fill); 2. Module Capex!B29 - Fluid management system
Racks per module |  |  | Model parameter | Pulls value from 0. Rack Profile!B37 | 2. Module Capex!B15 - Rack enclosures; 2. Module Capex!C15 - Rack enclosures; 2. Module Capex!B27 - Immersion tanks; 2. Module Capex!B28 - Dielectric fluid (initial fill); 2. Module Capex!B33 - Rack PDUs; 2. Module Capex!B47 - Per-rack monitoring
Servers per module |  |  | Model parameter | Pulls value from 0. Rack Profile!B38 | 2. Module Capex!B19 - Cold plate kits; 2. Module Capex!B22 - Manifolds & quick-connects
Module IT capacity (kW) |  |  | Define or calculate system capability | Pulls value from 0. Rack Profile!B40 | 2. Module Capex!B21 - CDU (capacity scaling); 2. Module Capex!B34 - Module power distribution; 2. Module Capex!B68 - Capex per IT kW (£/kW)
Captured heat (kWth) |  |  | Power or thermal capacity metric | Pulls value from 0. Rack Profile!B43 | 2. Module Capex!B40 - Heat exchanger (capacity scaling)
ENCLOSURE & STRUCTURE
Container shell |  | Fixed per module | Cost modular enclosure structure | Pulls value from 11. Reference Data!B71 | 2. Module Capex!B16 - SUBTOTAL: ENCLOSURE
Container fit-out |  | Fixed per module | Cost modular enclosure structure | Pulls value from 11. Reference Data!B72
Rack enclosures |  |  | Cost per-rack housing | Calculated from upstream values for Rack enclosures | 2. Module Capex!B16 - SUBTOTAL: ENCLOSURE
SUBTOTAL: ENCLOSURE |  |  | Subtotal enclosure costs for module | Sum of component values for SUBTOTAL: ENCLOSURE | 2. Module Capex!B60 - Applied to base infrastructure; 2. Module Capex!B63 - Base infrastructure; 6. System Capex!B14 - Enclosure & structure
DTC COOLING | Applies when cooling method = DTC |  | Section for DTC-specific equipment | Section header
Cold plate kits |  | Servers × £250/server | Cost DTC cooling hardware per server | Conditional logic for Cold plate kits | 2. Module Capex!B24 - SUBTOTAL: DTC COOLING
CDU (base) |  | Fixed per module | Cost coolant distribution unit | Conditional logic for CDU (base)
CDU (capacity scaling) |  | IT kW × £80/kW | Cost coolant distribution unit | Conditional logic for CDU (capacity scaling)
Manifolds & quick-connects |  | Servers × £150/server | Cost fluid distribution to racks | Conditional logic for Manifolds & quick-connects
Primary loop piping |  | Fixed per module | Cost primary cooling loop | Conditional logic for Primary loop piping | 2. Module Capex!B24 - SUBTOTAL: DTC COOLING
SUBTOTAL: DTC COOLING |  |  | Subtotal DTC cooling costs | Sum of component values for SUBTOTAL: DTC COOLING | 2. Module Capex!B60 - Applied to base infrastructure; 2. Module Capex!B63 - Base infrastructure; 6. System Capex!B15 - Cooling system
IMMERSION COOLING | Applies when cooling method = Immersion |  | Section for immersion-specific equipment | Section header
Immersion tanks |  | Racks × tank cost | Cost immersion cooling vessels | Conditional logic for Immersion tanks | 2. Module Capex!B30 - SUBTOTAL: IMMERSION COOLING
Dielectric fluid (initial fill) |  | Racks × volume × £/litre | Cost cooling fluid initial fill | Conditional logic for Dielectric fluid (initial fill)
Fluid management system |  | Fixed per module | Cost cooling fluid initial fill | Conditional logic for Fluid management system | 2. Module Capex!B30 - SUBTOTAL: IMMERSION COOLING
SUBTOTAL: IMMERSION COOLING |  |  | Subtotal immersion cooling costs | Sum of component values for SUBTOTAL: IMMERSION COOLING | 2. Module Capex!B60 - Applied to base infrastructure; 2. Module Capex!B63 - Base infrastructure; 6. System Capex!B15 - Cooling system
POWER DISTRIBUTION
Rack PDUs |  | Racks × £3,000/rack | Cost power distribution per rack | Calculated from upstream values for Rack PDUs | 2. Module Capex!B36 - SUBTOTAL: POWER
Module power distribution |  | IT kW × £180/kW | Cost module-level electrical | Calculated from upstream values for Module power distribution
Electrical panels & switchgear |  | Fixed per module | Cost electrical switching equipment | Pulls value from 11. Reference Data!B94 | 2. Module Capex!B36 - SUBTOTAL: POWER
SUBTOTAL: POWER |  |  | Subtotal power distribution costs | Sum of component values for SUBTOTAL: POWER | 2. Module Capex!B63 - Base infrastructure; 6. System Capex!B16 - Power distribution
THERMAL INTEGRATION
Primary heat exchanger (base) |  | Fixed per module | Cost thermal interface equipment | Pulls value from 11. Reference Data!B97 | 2. Module Capex!B43 - SUBTOTAL: THERMAL
Heat exchanger (capacity scaling) |  | Thermal kW × £25/kW | Cost thermal interface equipment | Calculated from upstream values for Heat exchanger (capacity scaling)
Thermal integration skid |  | Fixed per module | Cost heat delivery infrastructure | Pulls value from 11. Reference Data!B99
Instrumentation & sensors |  | Fixed per module | Cost monitoring equipment | Pulls value from 11. Reference Data!B100 | 2. Module Capex!B43 - SUBTOTAL: THERMAL
SUBTOTAL: THERMAL |  |  | Subtotal thermal integration costs | Sum of component values for SUBTOTAL: THERMAL | 2. Module Capex!B63 - Base infrastructure; 6. System Capex!B17 - Thermal integration
MONITORING & CONTROLS
BMS base system |  | Fixed per module | Cost building management system | Pulls value from 11. Reference Data!B103 | 2. Module Capex!B49 - SUBTOTAL: MONITORING
Per-rack monitoring |  | Racks × £500/rack | Cost per-rack monitoring | Calculated from upstream values for Per-rack monitoring
Network infrastructure |  | Fixed per module | Cost network infrastructure | Pulls value from 11. Reference Data!B105 | 2. Module Capex!B49 - SUBTOTAL: MONITORING
SUBTOTAL: MONITORING |  |  | Subtotal monitoring costs | Sum of component values for SUBTOTAL: MONITORING | 2. Module Capex!B63 - Base infrastructure; 6. System Capex!B18 - Monitoring & controls
HEAT PUMP (IF ENABLED) | From Module Criteria heat pump toggle |  | Model parameter | Section header
Heat pump CAPEX rate (£/kWth) | 600 |  | Financial input or calculation | Input parameter: Heat pump CAPEX rate (£/kWth) | 2. Module Capex!B53 - Heat pump unit
Heat pump unit |  |  | Cost heat pump equipment | Conditional logic for Heat pump unit | 2. Module Capex!B54 - Heat pump installation; 2. Module Capex!B56 - SUBTOTAL: HEAT PUMP; 3. Module Opex!B18 - Heat pump maintenance (£/yr)
Heat pump installation |  |  | Cost heat pump installation | Conditional logic for Heat pump installation
Heat pump controls |  |  | Cost heat pump control systems | Conditional logic for Heat pump controls | 2. Module Capex!B56 - SUBTOTAL: HEAT PUMP
SUBTOTAL: HEAT PUMP |  |  | Subtotal heat pump costs | Sum of component values for SUBTOTAL: HEAT PUMP | 2. Module Capex!B65 - Heat pump; 6. System Capex!B20 - Heat pump (if enabled)
COOLING METHOD PREMIUM
Premium rate (%) |  | From Rack Profile | Apply cooling technology cost premium | Formula: Premium rate (%) | 2. Module Capex!B60 - Applied to base infrastructure
Applied to base infrastructure |  | Enclosure + Cooling × Premium % | Model parameter | Formula: Applied to base infrastructure | 2. Module Capex!B64 - Cooling premium; 6. System Capex!B19 - Cooling method premium
TOTAL MODULE CAPEX
Base infrastructure |  |  | Model parameter | Calculated from upstream values for Base infrastructure | 2. Module Capex!B66 - TOTAL MODULE CAPEX; 3. Module Opex!B16 - Base maintenance (£/yr)
Cooling premium |  |  | Apply cooling technology cost premium | Formula: Cooling premium | 2. Module Capex!B66 - TOTAL MODULE CAPEX
Heat pump |  |  | Model parameter | Formula: Heat pump | 2. Module Capex!B66 - TOTAL MODULE CAPEX
TOTAL MODULE CAPEX |  |  | Sum all capital costs for investment analysis | Calculated from upstream values for TOTAL MODULE CAPEX | 2. Module Capex!B68 - Capex per IT kW (£/kW); 2. Module Capex!B69 - Capex per GPU (£/GPU); 3. Module Opex!B20 - Insurance (£/yr); 6. System Capex!B21 - TOTAL PER MODULE
Capex per IT kW (£/kW) |  |  | Calculate unit cost metric for comparison | Calculated from upstream values for Capex per IT kW (£/kW)
Capex per GPU (£/GPU) |  |  | Calculate unit cost metric for comparison | Calculated from upstream values for Capex per GPU (£/GPU)

## 3. Module Opex
MODULE OPEX |  |  |  | Intent | Explanation | Dependents
Annual operating expenditure for a single digital boiler module |  |  |  | Model parameter | Row label only
ELECTRICITY COSTS (TRIBE BEARS) |  |  |  | Financial input or calculation
Electricity rate (£/kWh) | 0.18 |  | Industrial electricity rate | Set electricity cost assumption | Input parameter: Electricity rate (£/kWh) | 3. Module Opex!B7 - Infrastructure power cost (£/yr); 3. Module Opex!B9 - Heat pump electricity (£/yr); 7. System Opex!B34 - Electricity rate (£/kWh)
Infrastructure power (from PUE) |  | PUE contribution - 1 | Pumps, controls, BMS, lighting (~5%) | Calculate cooling/support power draw | Formula: Infrastructure power (from PUE) | 3. Module Opex!B7 - Infrastructure power cost (£/yr)
Infrastructure power cost (£/yr) |  |  | IT kW × 5% × hours × £/kWh × util | Calculate cooling/support power draw | Formula: Infrastructure power cost (£/yr) | 3. Module Opex!B10 - SUBTOTAL: ELECTRICITY
Heat pump electricity (£/yr) |  |  | (HP kWth ÷ COP) × hours × util × £/kWh | Model heat pump operating expense | Conditional logic for Heat pump electricity (£/yr) | 3. Module Opex!B10 - SUBTOTAL: ELECTRICITY
SUBTOTAL: ELECTRICITY |  |  |  | Subtotal electricity costs | Calculated from upstream values for SUBTOTAL: ELECTRICITY | 3. Module Opex!B29 - TOTAL MODULE OPEX (£/yr); 7. System Opex!B14 - Electricity (infra + HP)
Note: Tenant rack power is pass-through (not included above) |  |  |  | Model parameter | Row label only
MAINTENANCE & INSURANCE
Base maintenance (% of base capex) | 3% |  |  | Model ongoing maintenance expense | Input parameter: Base maintenance (% of base capex) | 3. Module Opex!B16 - Base maintenance (£/yr)
Base maintenance (£/yr) |  |  |  | Model ongoing maintenance expense | Formula: Base maintenance (£/yr) | 3. Module Opex!B21 - SUBTOTAL: MAINTENANCE & INSURANCE
Heat pump maintenance (% of HP capex) | 2% |  |  | Model ongoing maintenance expense | Input parameter: Heat pump maintenance (% of HP capex) | 3. Module Opex!B18 - Heat pump maintenance (£/yr)
Heat pump maintenance (£/yr) |  |  |  | Model ongoing maintenance expense | Conditional logic for Heat pump maintenance (£/yr) | 3. Module Opex!B21 - SUBTOTAL: MAINTENANCE & INSURANCE
Insurance (% of total capex) | 1% |  |  | Model insurance expense | Input parameter: Insurance (% of total capex) | 3. Module Opex!B20 - Insurance (£/yr)
Insurance (£/yr) |  |  |  | Model insurance expense | Formula: Insurance (£/yr) | 3. Module Opex!B21 - SUBTOTAL: MAINTENANCE & INSURANCE
SUBTOTAL: MAINTENANCE & INSURANCE |  |  |  | Subtotal maintenance and insurance | Calculated from upstream values for SUBTOTAL: MAINTENANCE & INSURANCE | 3. Module Opex!B29 - TOTAL MODULE OPEX (£/yr); 7. System Opex!B15 - Maintenance & insurance
OTHER OPERATING COSTS
Site lease/licence (£/yr) | 15000 |  | Payment to industrial host (if any) | Model overhead operating expenses | Input assumption: Site lease/licence (£/yr) | 3. Module Opex!B27 - SUBTOTAL: OTHER
Remote monitoring & NOC (£/yr) | 12000 |  | 24/7 monitoring, allocated headcount | Model overhead operating expenses | Input assumption: Remote monitoring & NOC (£/yr)
Connectivity & admin (£/yr) | 8000 |  |  | Model overhead operating expenses | Input assumption: Connectivity & admin (£/yr) | 3. Module Opex!B27 - SUBTOTAL: OTHER
SUBTOTAL: OTHER |  |  |  | Subtotal other operating costs | Sum of component values for SUBTOTAL: OTHER | 3. Module Opex!B29 - TOTAL MODULE OPEX (£/yr); 7. System Opex!B16 - Other (site, NOC, admin)
TOTAL MODULE OPEX (£/yr) |  |  |  | Sum operating costs for profitability analysis | Calculated from upstream values for TOTAL MODULE OPEX (£/yr) | 7. System Opex!B17 - TOTAL PER MODULE
Note: Revenue and P&L calculations moved to System P&L sheet |  |  |  | Model parameter | Row label only
Module-level revenue is theoretical; actual revenue depends on buyer absorption |  |  |  | Model parameter | Row label only

## 4. Module Flow
MODULE FLOW ANALYSIS |  |  |  | Intent | Explanation | Dependents
Hydraulic calculations for a single digital boiler module |  |  |  | Model parameter | Row label only
CONSTANTS
Specific heat of water (kJ/kg·K) | 4.18 |  |  | Model parameter | Input parameter: Specific heat of water (kJ/kg·K) | 4. Module Flow!B14 - Mass flow rate (kg/s); 4. Module Flow!B24 - Mass flow rate (kg/s)
Water density (kg/L) | 1 |  |  | Model parameter | Flag enabled for Water density (kg/L) | 4. Module Flow!B15 - Volume flow rate (L/s); 4. Module Flow!B25 - Volume flow rate (L/s)
SOURCE LOOP (Servers → Heat Pump) |  |  |  | Model parameter
Thermal power (kWth) |  |  | Heat captured from servers | Pull heat load for flow calculations | Pulls value from 1. Module Criteria!B11 | 4. Module Flow!B14 - Mass flow rate (kg/s)
Inlet temperature (°C) |  |  |  | Define temperature differential for flow sizing | Pulls value from 1. Module Criteria!B12 | 4. Module Flow!B12 - Outlet temperature (°C)
Source loop ΔT (°C) |  | From cooling method (Reference Data) | Temperature drop across HP evaporator | Set temperature drop across heat source | Conditional logic for Source loop ΔT (°C) | 4. Module Flow!B12 - Outlet temperature (°C); 4. Module Flow!B14 - Mass flow rate (kg/s)
Outlet temperature (°C) |  |  |  | Define temperature differential for flow sizing | Calculated from upstream values for Outlet temperature (°C)
Mass flow rate (kg/s) |  |  |  | Calculate required fluid flow rate | Calculated from upstream values for Mass flow rate (kg/s) | 4. Module Flow!B15 - Volume flow rate (L/s)
Volume flow rate (L/s) |  |  |  | Convert to volumetric flow for pipe sizing | Calculated from upstream values for Volume flow rate (L/s) | 4. Module Flow!B16 - Volume flow rate (m³/hr); 4. Module Flow!B30 - Source loop pipe ID (mm)
Volume flow rate (m³/hr) |  |  |  | Convert to volumetric flow for pipe sizing | Calculated from upstream values for Volume flow rate (m³/hr)
SINK LOOP (Heat Pump → Industrial Partner) |  |  |  | Model parameter
Thermal power delivered (kWth) |  |  | With HP: includes compressor work | Pull heat load for flow calculations | Pulls value from 1. Module Criteria!B21 | 4. Module Flow!B24 - Mass flow rate (kg/s); 4. Module Flow!B37 - Thermal capacity (kWth)
Outlet temperature (°C) |  |  |  | Define temperature differential for flow sizing | Pulls value from 1. Module Criteria!B22 | 4. Module Flow!B22 - Return temperature (°C); 4. Module Flow!B38 - Delivery temperature (°C)
Sink loop ΔT (°C) | 10 |  | HP design assumption (process ΔT used in Buyer Profile) | Model parameter | Input parameter: Sink loop ΔT (°C) | 4. Module Flow!B22 - Return temperature (°C); 4. Module Flow!B24 - Mass flow rate (kg/s)
Return temperature (°C) |  |  |  | Calculate return water temperature | Calculated from upstream values for Return temperature (°C)
Mass flow rate (kg/s) |  |  |  | Calculate required fluid flow rate | Calculated from upstream values for Mass flow rate (kg/s) | 4. Module Flow!B25 - Volume flow rate (L/s)
Volume flow rate (L/s) |  |  |  | Convert to volumetric flow for pipe sizing | Calculated from upstream values for Volume flow rate (L/s) | 4. Module Flow!B26 - Volume flow rate (m³/hr); 4. Module Flow!B31 - Sink loop pipe ID (mm)
Volume flow rate (m³/hr) |  |  |  | Convert to volumetric flow for pipe sizing | Calculated from upstream values for Volume flow rate (m³/hr) | 4. Module Flow!B39 - Flow capacity (m³/hr); 5. Buyer Profile!B30 - Module flow capacity (m³/hr)
PIPE SIZING GUIDANCE
Design velocity (m/s) | 2 |  | Typical: 1.5-3 m/s | Model parameter | Input parameter: Design velocity (m/s) | 4. Module Flow!B30 - Source loop pipe ID (mm); 4. Module Flow!B31 - Sink loop pipe ID (mm)
Source loop pipe ID (mm) |  |  |  | Size piping for required flow | Square root calculation for Source loop pipe ID (mm) | 4. Module Flow!B33 - Source loop - nearest DN
Sink loop pipe ID (mm) |  |  |  | Size piping for required flow | Square root calculation for Sink loop pipe ID (mm) | 4. Module Flow!B34 - Sink loop - nearest DN
Source loop - nearest DN |  |  |  | Select standard pipe size | Conditional logic for Source loop - nearest DN
Sink loop - nearest DN |  |  |  | Select standard pipe size | Conditional logic for Sink loop - nearest DN
MODULE HYDRAULIC SUMMARY
Thermal capacity (kWth) |  |  |  | Summarise module heat delivery capability | Formula: Thermal capacity (kWth)
Delivery temperature (°C) |  |  |  | Summarise module output temperature | Formula: Delivery temperature (°C)
Flow capacity (m³/hr) |  |  |  | Summarise module flow capability | Formula: Flow capacity (m³/hr)

## 5. Buyer Profile
BUYER PROFILE |  |  |  | Intent | Explanation | Dependents
Select an industrial process to see system requirements |  |  |  | Model parameter | Row label only
HARDWARE CONFIGURATION
Chipset |  |  |  | Pull system configuration for context | Pulls value from 0. Rack Profile!B6
Cooling method |  |  |  | Pull system configuration for context | Pulls value from 0. Rack Profile!B17
GPUs per module |  |  |  | Pull system configuration for context | Pulls value from 0. Rack Profile!B39
Module IT capacity (kW) |  |  |  | Pull module size for calculations | Pulls value from 0. Rack Profile!B40
PROCESS SELECTION
Select process | Pasteurisation - Medium |  |  | User input to select industrial heat buyer | Text value for Select process | 5. Buyer Profile!B14 - Process name; 5. Buyer Profile!B15 - Size category; 5. Buyer Profile!B16 - Required temperature (°C); 5. Buyer Profile!B17 - Heat demand (kWth); 5. Buyer Profile!B18 - Operating hours/year; 5. Buyer Profile!B19 - Notes; 5. Buyer Profile!B20 - Source:; 5. Buyer Profile!B21 - Source URL:; 5. Buyer Profile!B24 - Process ΔT (°C); 6. System Capex!B10 - Selected buyer profile; ... and 3 more
SELECTED PROCESS PARAMETERS
Process name |  |  |  | Look up selected process details | Lookup with error handling for Process name
Size category |  |  |  | Identify process scale | Lookup with error handling for Size category
Required temperature (°C) |  |  |  | Pull buyer's temperature requirement | Lookup with error handling for Required temperature (°C) | 5. Buyer Profile!B32 - Temperature compatible?; 5. Buyer Profile!B69 - Heat pump required?; 5. Buyer Profile!B70 - Temperature lift required (K); 8. System Flow!B14 - Required temperature (°C)
Heat demand (kWth) |  |  |  | Pull buyer's thermal load requirement | Lookup with error handling for Heat demand (kWth) | 5. Buyer Profile!B23 - Annual heat demand (MWh); 5. Buyer Profile!B25 - Required flow rate (m³/hr); 5. Buyer Profile!B33 - Modules needed (thermal); 5. Buyer Profile!B42 - Thermal utilisation (%); 5. Buyer Profile!B47 - Buyer heat absorption (kWth); 6. System Capex!B49 - Capex per kWth delivered (£/kWth); 8. System Flow!B15 - Required thermal load (kWth)
Operating hours/year |  |  |  | Pull buyer's usage pattern | Lookup with error handling for Operating hours/year | 5. Buyer Profile!B23 - Annual heat demand (MWh); 7. System Opex!B33 - Annual operating hours; 8. System Flow!B23 - Annual heat supply (MWh); 9. System P&L!B14 - Operating hours/year; 9. System P&L!B21 - Buyer operating hours/year
Notes |  |  |  | Pull process context information | Lookup with error handling for Notes
Source: |  |  |  | Reference data provenance | Lookup with error handling for Source:
Source URL: |  |  |  | Reference data provenance | Lookup with error handling for Source URL:
CALCULATED DEMAND
Annual heat demand (MWh) |  |  |  | Pull buyer's thermal load requirement | Calculated from upstream values for Annual heat demand (MWh) | 8. System Flow!B17 - Annual heat demand (MWh)
Process ΔT (°C) |  | From Process Library (default 10 if not found) | Conservative assumption for flow calculation | Pull process temperature differential | Lookup with error handling for Process ΔT (°C) | 5. Buyer Profile!B25 - Required flow rate (m³/hr)
Required flow rate (m³/hr) |  |  |  | Calculate buyer's flow requirement | Calculated from upstream values for Required flow rate (m³/hr) | 5. Buyer Profile!B34 - Modules if flow-constrained (refere...; 5. Buyer Profile!B36 - Flow deficit (m³/hr); 5. Buyer Profile!B37 - Flow ratio (buyer/system); 5. Buyer Profile!B43 - Flow utilisation (%); 5. Buyer Profile!B87 - Flow requirement met?; 8. System Flow!B16 - Required flow rate (m³/hr)
SYSTEM SIZING
Module thermal capacity (kWth) |  |  |  | Pull single module heat output | Pulls value from 1. Module Criteria!B21 | 5. Buyer Profile!B33 - Modules needed (thermal); 5. Buyer Profile!B40 - System thermal capacity (kWth)
Module delivery temp (°C) |  |  |  | Pull module output temperature | Pulls value from 1. Module Criteria!B22 | 5. Buyer Profile!B32 - Temperature compatible?
Module flow capacity (m³/hr) |  |  |  | Pull single module flow capacity | Pulls value from 4. Module Flow!B26 | 5. Buyer Profile!B34 - Modules if flow-constrained (refere...; 5. Buyer Profile!B36 - Flow deficit (m³/hr); 5. Buyer Profile!B37 - Flow ratio (buyer/system); 5. Buyer Profile!B41 - System flow capacity (m³/hr)
Temperature compatible? |  |  |  | Check if system meets buyer temp needs | Conditional logic for Temperature compatible?
Modules needed (thermal) |  |  |  | Calculate modules for thermal demand | Rounded calculation for Modules needed (thermal) | 5. Buyer Profile!B35 - MODULES REQUIRED
Modules if flow-constrained (reference) |  | Informational only - flow handled via hydraulics |  | Calculate modules if flow-constrained | Rounded calculation for Modules if flow-constrained (reference)
MODULES REQUIRED |  | Thermal sizing only - flow deficit handled separately | Higher of thermal or flow requirement | Determine final module count for system sizing | Formula: MODULES REQUIRED | 5. Buyer Profile!B36 - Flow deficit (m³/hr); 5. Buyer Profile!B37 - Flow ratio (buyer/system); 5. Buyer Profile!B40 - System thermal capacity (kWth); 5. Buyer Profile!B41 - System flow capacity (m³/hr); 5. Buyer Profile!B64 - Total modules required; 5. Buyer Profile!B65 - Total IT capacity (kW); 5. Buyer Profile!B71 - Heat pump units; 5. Buyer Profile!B72 - Total HP capacity (kWth); 5. Buyer Profile!B76 - Source loop pumps; 5. Buyer Profile!B77 - Sink loop pumps; ... and 9 more
Flow deficit (m³/hr) |  | Buyer flow need minus system flow capacity |  | Identify shortfall requiring augmentation | Bounded value for Flow deficit (m³/hr) | 5. Buyer Profile!B81 - Flow augmentation pump (m³/hr); 5. Buyer Profile!B82 - Mixing valve required?; 5. Buyer Profile!B84 - Augmentation pumps required; 6. System Capex!B35 - Flow deficit (m³/hr)
Flow ratio (buyer/system) |  | >1 means hydraulic augmentation needed |  | Compare buyer need to system capacity | Conditional logic for Flow ratio (buyer/system) | 5. Buyer Profile!B44 - Hydraulic augmentation needed?
UTILISATION ANALYSIS | [5 empty] | 8. System Flow!B22 - System flow capacity (m³/hr)
System thermal capacity (kWth) |  |  |  | Calculate total system heat output | Calculated from upstream values for System thermal capacity (kWth) | 5. Buyer Profile!B42 - Thermal utilisation (%); 5. Buyer Profile!B46 - System heat generation (kWth); 5. Buyer Profile!B47 - Buyer heat absorption (kWth); 5. Buyer Profile!B73 - HP electrical demand (kW); 8. System Flow!B32 - Thermal utilisation
System flow capacity (m³/hr) |  |  |  | Calculate total system flow | Calculated from upstream values for System flow capacity (m³/hr) | 5. Buyer Profile!B43 - Flow utilisation (%); 5. Buyer Profile!B78 - Total system flow (m³/hr); 5. Buyer Profile!B79 - Header pipe size estimate (DN); 5. Buyer Profile!B86 - Augmented system flow (m³/hr); 8. System Flow!B33 - Flow utilisation
Thermal utilisation (%) |  |  |  | Measure how much heat capacity is used | Calculated from upstream values for Thermal utilisation (%) | 8. System Flow!B34 - Binding constraint
Flow utilisation (%) |  | Required flow / augmented system flow |  | Measure how much flow capacity is used | Conditional logic for Flow utilisation (%)
Hydraulic augmentation needed? |  | Flow ratio > 1 means buyer needs more flow than modules provide |  | Flag if pumps needed for flow boost | Conditional logic for Hydraulic augmentation needed?
HEAT BALANCE
System heat generation (kWth) |  | Total heat from modules |  | Total heat produced by system | Formula: System heat generation (kWth) | 5. Buyer Profile!B48 - Excess heat (kWth); 5. Buyer Profile!B49 - Excess heat (%); 9. System P&L!B23 - Theoretical heat output (kWth)
Buyer heat absorption (kWth) |  | Limited by buyer demand |  | Actual heat buyer can use | Bounded value for Buyer heat absorption (kWth) | 5. Buyer Profile!B48 - Excess heat (kWth); 9. System P&L!B26 - Actual buyer absorption (kWth)
Excess heat (kWth) |  | Requires rejection cooling |  | Heat requiring rejection | Bounded value for Excess heat (kWth) | 5. Buyer Profile!B49 - Excess heat (%); 5. Buyer Profile!B50 - Heat rejection required?; 5. Buyer Profile!B51 - Rejection method; 5. Buyer Profile!B52 - Rejection capacity required (kWth); 7. System Opex!B26 - Excess heat (kWth)
Excess heat (%) |  | Proportion of generation not sold |  | Heat requiring rejection | Conditional logic for Excess heat (%)
Heat rejection required? |  |  |  | Size and cost rejection equipment | Conditional logic for Heat rejection required?
Rejection method |  | Thresholds from Reference Data sheet |  | Select appropriate rejection technology | Conditional logic for Rejection method | 5. Buyer Profile!B53 - Rejection capex rate (£/kWth); 5. Buyer Profile!B54 - Rejection opex rate (£/kWth/yr)
Rejection capacity required (kWth) |  | Must handle 100% of system output if buyer goes offline |  | Size rejection equipment | Formula: Rejection capacity required (kWth) | 5. Buyer Profile!B55 - Rejection capex (£); 5. Buyer Profile!B56 - Annual rejection opex (£/yr); 6. System Capex!B30 - Rejection capacity required (kWth)
Rejection capex rate (£/kWth) |  | Capex rates from Reference Data sheet |  | Cost heat rejection | Conditional logic for Rejection capex rate (£/kWth) | 5. Buyer Profile!B55 - Rejection capex (£); 6. System Capex!B31 - Rejection capex rate (£/kWth)
Rejection opex rate (£/kWth/yr) |  | Opex rates from Reference Data sheet |  | Cost heat rejection | Conditional logic for Rejection opex rate (£/kWth/yr) | 5. Buyer Profile!B56 - Annual rejection opex (£/yr); 7. System Opex!B27 - Rejection running cost (£/kWth/yr)
Rejection capex (£) |  | Capacity × capex rate (sized for worst case) |  | Cost heat rejection | Calculated from upstream values for Rejection capex (£)
Annual rejection opex (£/yr) |  | ACTUAL excess heat × opex rate (normal operation) |  | Cost heat rejection | Calculated from upstream values for Annual rejection opex (£/yr)
HARDWARE DEPENDENCIES
Equipment requirements implied by buyer selection |  |  |  | Model parameter | Row label only
Module Configuration |  |  |  | Model parameter | Row label only
Total modules required |  |  |  | Determine final module count | Formula: Total modules required
Total IT capacity (kW) |  |  |  | Summarise compute capacity | Calculated from upstream values for Total IT capacity (kW) | 5. Buyer Profile!B66 - Total rack units (42U racks @ 10kW); 5. Buyer Profile!B91 - IT load (kW); 5. Buyer Profile!B92 - Cooling infrastructure (kW)
Total rack units (42U racks @ 10kW) |  | Based on IT capacity (10kW per 42U rack) |  | Sum components for analysis | Rounded calculation for Total rack units (42U racks @ 10kW) | 5. Buyer Profile!B107 - 42U server racks
Heat Pump Requirements |  |  |  | Size circulation equipment | Row label only
Heat pump required? |  |  |  | Check if HP needed for buyer | Conditional logic for Heat pump required?
Temperature lift required (K) |  |  |  | Calculate required HP boost | Conditional logic for Temperature lift required (K)
Heat pump units |  | 1 HP per module |  | Count HP equipment needed | Formula: Heat pump units | 5. Buyer Profile!B106 - Heat pump units
Total HP capacity (kWth) |  |  |  | Size total HP thermal capacity | Calculated from upstream values for Total HP capacity (kWth)
HP electrical demand (kW) |  | HP output / COP |  | Calculate HP power consumption | Conditional logic for HP electrical demand (kW) | 5. Buyer Profile!B93 - Heat pump load (kW)
Hydraulic Infrastructure |  |  |  | Model parameter | Row label only
Source loop pumps |  | 1 per module |  | Reference data provenance | Formula: Source loop pumps | 5. Buyer Profile!B108 - Source circulation pumps
Sink loop pumps |  | 1 per module |  | Size circulation equipment | Formula: Sink loop pumps | 5. Buyer Profile!B109 - Sink circulation pumps
Total system flow (m³/hr) |  |  |  | Sum components for analysis | Formula: Total system flow (m³/hr)
Header pipe size estimate (DN) |  | Based on 2 m/s design velocity |  | Size main distribution piping | Conditional logic for Header pipe size estimate (DN)
Buffer tank recommended? |  |  |  | Flag if thermal buffer needed | Conditional logic for Buffer tank recommended? | 5. Buyer Profile!B111 - Buffer tank
Flow augmentation pump (m³/hr) |  | Sized for flow deficit |  | Size circulation equipment | Formula: Flow augmentation pump (m³/hr)
Mixing valve required? |  | Blends supply with return for higher flow |  | Flag if temperature control needed | Conditional logic for Mixing valve required?
Augmentation pump power (kW) |  | Actual pump capacity × kW/m³/hr |  | Size circulation equipment | Calculated from upstream values for Augmentation pump power (kW) | 7. System Opex!B32 - Augmentation pump power (kW)
Augmentation pumps required |  | Rounded up to whole pumps |  | Size circulation equipment | Conditional logic for Augmentation pumps required | 5. Buyer Profile!B85 - Augmentation pump capacity (m³/hr); 5. Buyer Profile!B113 - Flow augmentation pumps; 5. Buyer Profile!B114 - Mixing valves; 6. System Capex!B36 - Augmentation pumps required
Augmentation pump capacity (m³/hr) |  | Pumps × standard capacity |  | Size circulation equipment | Calculated from upstream values for Augmentation pump capacity (m³/hr) | 5. Buyer Profile!B83 - Augmentation pump power (kW); 5. Buyer Profile!B86 - Augmented system flow (m³/hr); 7. System Opex!B31 - Augmentation pump capacity (m³/hr)
Augmented system flow (m³/hr) |  | Base module flow + augmentation |  | Fluid flow parameter for hydraulic design | Calculated from upstream values for Augmented system flow (m³/hr) | 5. Buyer Profile!B43 - Flow utilisation (%); 5. Buyer Profile!B87 - Flow requirement met?
Flow requirement met? |  | Augmented flow >= required flow |  | Fluid flow parameter for hydraulic design | Conditional logic for Flow requirement met?
Electrical Infrastructure |  |  |  | Model parameter | Row label only
IT load (kW) |  |  |  | Calculate IT electrical demand | Formula: IT load (kW) | 5. Buyer Profile!B94 - Total electrical demand (kW)
Cooling infrastructure (kW) |  | 5% of IT load for pumps/controls |  | Calculate cooling electrical demand | Calculated from upstream values for Cooling infrastructure (kW) | 5. Buyer Profile!B94 - Total electrical demand (kW)
Heat pump load (kW) |  |  |  | Size circulation equipment | Formula: Heat pump load (kW) | 5. Buyer Profile!B94 - Total electrical demand (kW)
Total electrical demand (kW) |  |  |  | Sum all electrical loads | Calculated from upstream values for Total electrical demand (kW) | 5. Buyer Profile!B95 - Grid connection (kVA @ 0.9 PF)
Grid connection (kVA @ 0.9 PF) |  | Rounded to nearest 10 kVA |  | Size grid supply requirement | Rounded calculation for Grid connection (kVA @ 0.9 PF)
Space Requirements |  |  |  | Model parameter
Module footprint each (m²) | 15 | Typical 20ft container |  | Calculate space requirements | Input parameter: Module footprint each (m²) | 5. Buyer Profile!B99 - Total module footprint (m²)
Total module footprint (m²) |  |  |  | Calculate space requirements | Calculated from upstream values for Total module footprint (m²) | 5. Buyer Profile!B101 - Total site area (m²)
Plant room allowance (m²) |  | For headers, buffer, controls |  | Allocate support equipment space | Conditional logic for Plant room allowance (m²) | 5. Buyer Profile!B101 - Total site area (m²)
Total site area (m²) |  | Excluding access/clearances |  | Calculate space requirements | Calculated from upstream values for Total site area (m²)
BILL OF MATERIALS SUMMARY
Item | Qty | Notes |  | Model parameter | Text value for Item
Modular DC units (250kW IT) |  | Containerised data centre |  | Generate equipment list for procurement | Formula: Modular DC units (250kW IT)
Heat pump units |  | Industrial HTHP, CO2 or NH3 |  | Count HP equipment needed | Formula: Heat pump units
42U server racks |  | @ 10kW per rack |  | Generate equipment list for procurement | Formula: 42U server racks
Source circulation pumps |  | Grundfos/Wilo industrial |  | Reference data provenance | Formula: Source circulation pumps
Sink circulation pumps |  | Variable speed |  | Size circulation equipment | Formula: Sink circulation pumps
Plate heat exchangers |  | Alfa Laval or equiv |  | Model parameter | Formula: Plate heat exchangers
Buffer tank |  | If multi-module |  | Flag if thermal buffer needed | Conditional logic for Buffer tank
BMS/Controls package | 1 | Central monitoring |  | Model parameter | Flag enabled for BMS/Controls package
Flow augmentation pumps |  | For flow deficit (if any) |  | Size circulation equipment | Formula: Flow augmentation pumps
Mixing valves |  | 1 if augmentation needed |  | Flag if temperature control needed | Conditional logic for Mixing valves

## 6. System Capex
SYSTEM CAPEX |  |  | Intent | Explanation | Dependents
Capital expenditure for complete system serving selected buyer |  |  | Model parameter | Row label only
HARDWARE CONFIGURATION
Chipset |  |  | Model parameter | Pulls value from 0. Rack Profile!B6
Cooling method |  |  | Model parameter | Pulls value from 0. Rack Profile!B17
GPUs per module |  |  | Model parameter | Pulls value from 0. Rack Profile!B39
SYSTEM CONFIGURATION
Selected buyer profile |  |  | Model parameter | Pulls value from 5. Buyer Profile!B11
Modules required |  |  | Pull module count from buyer sizing | Pulls value from 5. Buyer Profile!B35 | 6. System Capex!B24 - Total module capex; 6. System Capex!B27 - Integration & commissioning; 6. System Capex!B48 - Capex per IT kW (£/kW)
MODULE CAPEX (per unit) |  |  | Model parameter
Enclosure & structure |  |  | Pull per-module enclosure cost | Pulls value from 2. Module Capex!B16
Cooling system |  | DTC or Immersion (whichever applies) | Pull per-module cooling cost | Formula: Cooling system
Power distribution |  |  | Pull per-module power cost | Pulls value from 2. Module Capex!B36
Thermal integration |  |  | Pull per-module thermal cost | Pulls value from 2. Module Capex!B43
Monitoring & controls |  |  | Pull per-module monitoring cost | Pulls value from 2. Module Capex!B49
Cooling method premium |  | From Rack Profile | Pull cooling technology premium | Pulls value from 2. Module Capex!B60
Heat pump (if enabled) |  |  | Pull per-module HP cost | Pulls value from 2. Module Capex!B56
TOTAL PER MODULE |  |  | Sum per-module costs for scaling | Pulls value from 2. Module Capex!B66 | 6. System Capex!B24 - Total module capex
Total module capex |  |  | Calculate all modules cost | Calculated from upstream values for Total module capex | 6. System Capex!B26 - Shared infrastructure (£); 6. System Capex!B43 - Base system capex (excl. rejection)
Shared infrastructure (%) | 5% | Common civils, shared services (scales with modules) | Add common infrastructure cost | Input parameter: Shared infrastructure (%) | 6. System Capex!B26 - Shared infrastructure (£)
Shared infrastructure (£) |  |  | Add common infrastructure cost | Calculated from upstream values for Shared infrastructure (£) | 6. System Capex!B43 - Base system capex (excl. rejection)
Integration & commissioning |  | £25k per additional module | Add system integration cost | Conditional logic for Integration & commissioning | 6. System Capex!B43 - Base system capex (excl. rejection)
Additional capex for cooling
Rejection capacity required (kWth) |  |  | Add heat rejection equipment cost | Pulls value from 5. Buyer Profile!B52 | 6. System Capex!B32 - Heat rejection capex
Rejection capex rate (£/kWth) |  |  | Add heat rejection equipment cost | Pulls value from 5. Buyer Profile!B53 | 6. System Capex!B32 - Heat rejection capex
Heat rejection capex |  | Sized for 100% rejection (buyer offline scenario) | Add heat rejection equipment cost | Conditional logic for Heat rejection capex | 6. System Capex!B44 - Heat rejection capex
HYDRAULIC AUGMENTATION
Flow deficit (m³/hr) |  |  | Fluid flow parameter for hydraulic design | Pulls value from 5. Buyer Profile!B36 | 6. System Capex!B38 - Mixing valve + controls; 6. System Capex!B39 - Pipe upsizing allowance
Augmentation pumps required |  |  | Add flow augmentation cost | Pulls value from 5. Buyer Profile!B84 | 6. System Capex!B37 - Augmentation pump capex
Augmentation pump capex |  | Pumps × capacity × £/m³/hr | Add flow augmentation cost | Calculated from upstream values for Augmentation pump capex | 6. System Capex!B40 - SUBTOTAL: HYDRAULIC AUGMENTATION
Mixing valve + controls |  |  | Model parameter | Conditional logic for Mixing valve + controls
Pipe upsizing allowance |  | If flow deficit > 20 m³/hr | Model parameter | Conditional logic for Pipe upsizing allowance | 6. System Capex!B40 - SUBTOTAL: HYDRAULIC AUGMENTATION
SUBTOTAL: HYDRAULIC AUGMENTATION |  |  | Subtotal flow augmentation costs | Sum of component values for SUBTOTAL: HYDRAULIC AUGMENTATION | 6. System Capex!B45 - Hydraulic augmentation capex
TOTAL SYSTEM CAPEX
Base system capex (excl. rejection) |  | Module + shared + integration costs | Add heat rejection equipment cost | Calculated from upstream values for Base system capex (excl. rejection) | 6. System Capex!B46 - TOTAL SYSTEM CAPEX
Heat rejection capex |  |  | Add heat rejection equipment cost | Formula: Heat rejection capex | 6. System Capex!B46 - TOTAL SYSTEM CAPEX
Hydraulic augmentation capex |  |  | Add flow augmentation cost | Formula: Hydraulic augmentation capex | 6. System Capex!B46 - TOTAL SYSTEM CAPEX
TOTAL SYSTEM CAPEX |  |  | Sum complete investment requirement | Calculated from upstream values for TOTAL SYSTEM CAPEX | 6. System Capex!B48 - Capex per IT kW (£/kW); 6. System Capex!B49 - Capex per kWth delivered (£/kWth); 9. System P&L!B48 - Total system capex (£)
Capex per IT kW (£/kW) |  |  | Calculate unit cost metric | Calculated from upstream values for Capex per IT kW (£/kW)
Capex per kWth delivered (£/kWth) |  |  | Calculate unit cost metric | Calculated from upstream values for Capex per kWth delivered (£/kWth)

## 7. System Opex
SYSTEM OPEX |  |  |  | Intent | Explanation | Dependents
Annual operating costs and revenue for complete system |  |  |  | Financial input or calculation | Row label only
HARDWARE CONFIGURATION
Chipset |  |  |  | Model parameter | Pulls value from 0. Rack Profile!B6
Cooling method |  |  |  | Model parameter | Pulls value from 0. Rack Profile!B17
GPUs per module |  |  |  | Model parameter | Pulls value from 0. Rack Profile!B39
SYSTEM CONFIGURATION
Selected buyer profile |  |  |  | Model parameter | Pulls value from 5. Buyer Profile!B11
Modules in system |  |  |  | Pull module count | Pulls value from 5. Buyer Profile!B35 | 7. System Opex!B20 - Total module opex
MODULE OPEX (per unit, £/yr) |  |  |  | Financial input or calculation
Electricity (infra + HP) |  |  |  | Pull per-module electricity cost | Pulls value from 3. Module Opex!B10
Maintenance & insurance |  |  |  | Pull per-module maintenance cost | Pulls value from 3. Module Opex!B21
Other (site, NOC, admin) |  |  |  | Pull per-module overhead cost | Pulls value from 3. Module Opex!B27
TOTAL PER MODULE |  |  |  | Sum per-module opex for scaling | Pulls value from 3. Module Opex!B29 | 7. System Opex!B20 - Total module opex
SYSTEM OPEX (all modules, £/yr) |  |  |  | Pull module count
Total module opex |  |  |  | Calculate all modules opex | Calculated from upstream values for Total module opex | 7. System Opex!B22 - Shared overhead (£/yr); 7. System Opex!B23 - Base system opex (excl. rejection)
Shared overhead (%) | 5% |  | Central management allocation | Add common operating costs | Input parameter: Shared overhead (%) | 7. System Opex!B22 - Shared overhead (£/yr)
Shared overhead (£/yr) |  |  |  | Add common operating costs | Calculated from upstream values for Shared overhead (£/yr) | 7. System Opex!B23 - Base system opex (excl. rejection)
Base system opex (excl. rejection) |  | Module + shared overhead costs |  | Sum base operating costs | Calculated from upstream values for Base system opex (excl. rejection) | 7. System Opex!B29 - Heat rejection uplift (%); 7. System Opex!B37 - TOTAL SYSTEM OPEX; 9. System P&L!B39 - Base system opex (£/yr)
HEAT REJECTION OPEX
Excess heat (kWth) |  | Actual excess heat in normal operation |  | Pull heat requiring rejection | Pulls value from 5. Buyer Profile!B48 | 7. System Opex!B28 - Heat rejection opex (£/yr)
Rejection running cost (£/kWth/yr) |  | Variable rate from Buyer Profile based on rejection method |  | Add heat rejection operating cost | Pulls value from 5. Buyer Profile!B54 | 7. System Opex!B28 - Heat rejection opex (£/yr)
Heat rejection opex (£/yr) |  |  |  | Add heat rejection operating cost | Conditional logic for Heat rejection opex (£/yr) | 7. System Opex!B29 - Heat rejection uplift (%); 7. System Opex!B37 - TOTAL SYSTEM OPEX; 9. System P&L!B40 - Heat rejection opex (£/yr)
Heat rejection uplift (%) |  | Additional opex for cooling |  | Add heat rejection operating cost | Conditional logic for Heat rejection uplift (%)
HYDRAULIC AUGMENTATION OPEX
Augmentation pump capacity (m³/hr) |  |  |  | Add pump operating cost | Pulls value from 5. Buyer Profile!B85
Augmentation pump power (kW) |  |  |  | Add pump operating cost | Pulls value from 5. Buyer Profile!B83 | 7. System Opex!B35 - Augmentation pump electricity (£/yr...
Annual operating hours |  | From buyer operating profile |  | Model parameter | Pulls value from 5. Buyer Profile!B18 | 7. System Opex!B35 - Augmentation pump electricity (£/yr...
Electricity rate (£/kWh) |  |  |  | Financial input or calculation | Pulls value from 3. Module Opex!B5 | 7. System Opex!B35 - Augmentation pump electricity (£/yr...
Augmentation pump electricity (£/yr) |  |  |  | Add pump operating cost | Calculated from upstream values for Augmentation pump electricity (£/yr) | 7. System Opex!B37 - TOTAL SYSTEM OPEX; 9. System P&L!B41 - Hydraulic augmentation opex (£/yr)
TOTAL SYSTEM OPEX |  |  |  | Sum complete operating costs | Calculated from upstream values for TOTAL SYSTEM OPEX | 9. System P&L!B42 - TOTAL OPEX (£/yr)
Note: Revenue and P&L calculations moved to System P&L sheet |  |  |  | Model parameter | Row label only
See "9. System P&L" for actual revenue based on buyer heat absorption |  |  |  | Model parameter | Row label only

## 8. System Flow
SYSTEM FLOW ANALYSIS |  |  |  | Intent | Explanation | Dependents
Hydraulic analysis for complete system serving selected buyer |  |  |  | Model parameter | Row label only
HARDWARE CONFIGURATION
Chipset |  |  |  | Model parameter | Pulls value from 0. Rack Profile!B6
Cooling method |  |  |  | Model parameter | Pulls value from 0. Rack Profile!B17
Capture temperature (°C) |  |  |  | Pull heat source temperature | Pulls value from 0. Rack Profile!B21
SYSTEM CONFIGURATION
Selected buyer profile |  |  |  | Pull sizing from buyer analysis | Pulls value from 5. Buyer Profile!B11
Modules in system |  |  |  | Pull sizing from buyer analysis | Pulls value from 5. Buyer Profile!B35
BUYER REQUIREMENTS
Required temperature (°C) |  |  |  | Pull buyer temperature requirement | Pulls value from 5. Buyer Profile!B16 | 8. System Flow!B26 - Temperature (°C)
Required thermal load (kWth) |  |  |  | Pull buyer heat requirement | Pulls value from 5. Buyer Profile!B17 | 8. System Flow!B27 - Thermal load (kWth); 8. System Flow!B36 - Spare capacity (kWth)
Required flow rate (m³/hr) |  |  |  | Pull buyer flow requirement | Pulls value from 5. Buyer Profile!B25 | 8. System Flow!B28 - Flow rate (m³/hr); 8. System Flow!B37 - Spare capacity (m³/hr); 8. System Flow!B41 - Main header pipe ID (mm)
Annual heat demand (MWh) |  |  |  | Pull buyer annual energy need | Pulls value from 5. Buyer Profile!B23 | 8. System Flow!B29 - Annual energy (MWh)
SYSTEM CAPACITY
Delivery temperature (°C) |  |  |  | Pull system output temperature | Pulls value from 1. Module Criteria!B22 | 8. System Flow!C26 - Temperature (°C)
System thermal capacity (kWth) |  |  |  | Pull system heat capacity | Pulls value from 5. Buyer Profile!B38 | 8. System Flow!B23 - Annual heat supply (MWh); 8. System Flow!C27 - Thermal load (kWth); 8. System Flow!B36 - Spare capacity (kWth)
System flow capacity (m³/hr) |  |  |  | Pull system flow capacity | Pulls value from 5. Buyer Profile!B39 | 8. System Flow!C28 - Flow rate (m³/hr); 8. System Flow!B37 - Spare capacity (m³/hr)
Annual heat supply (MWh) |  | kWth × buyer hours ÷ 1000 |  | Calculate annual heat available | Calculated from upstream values for Annual heat supply (MWh) | 8. System Flow!C29 - Annual energy (MWh)
SUPPLY vs DEMAND MATCH | Required | Supplied | Match? | Compare system capability to buyer need | Text value for SUPPLY vs DEMAND MATCH
Temperature (°C) |  |  |  | Temperature parameter for thermal design | Formula: Temperature (°C) | 8. System Flow!D26 - Temperature (°C)
Thermal load (kWth) |  |  |  | Power or thermal capacity metric | Formula: Thermal load (kWth) | 8. System Flow!D27 - Thermal load (kWth)
Flow rate (m³/hr) |  |  |  | Efficiency or utilisation metric | Formula: Flow rate (m³/hr) | 8. System Flow!D28 - Flow rate (m³/hr)
Annual energy (MWh) |  |  |  | Model parameter | Formula: Annual energy (MWh) | 8. System Flow!D29 - Annual energy (MWh)
UTILISATION SUMMARY
Thermal utilisation |  |  |  | Show capacity usage metrics | Pulls value from 5. Buyer Profile!B40
Flow utilisation |  |  |  | Show capacity usage metrics | Pulls value from 5. Buyer Profile!B41
Binding constraint |  |  |  | Identify limiting factor | Pulls value from 5. Buyer Profile!B42
Spare capacity (kWth) |  |  |  | Show available headroom | Calculated from upstream values for Spare capacity (kWth)
Spare capacity (m³/hr) |  |  |  | Show available headroom | Calculated from upstream values for Spare capacity (m³/hr)
SYSTEM PIPE SIZING
Design velocity (m/s) | 2 |  |  | Model parameter | Input parameter: Design velocity (m/s) | 8. System Flow!B41 - Main header pipe ID (mm)
Main header pipe ID (mm) |  |  |  | Size main distribution piping | Square root calculation for Main header pipe ID (mm) | 8. System Flow!B42 - Nearest DN size
Nearest DN size |  |  |  | Select standard pipe size | Conditional logic for Nearest DN size

## 9. System P&L
SYSTEM P&L |  | Intent | Explanation | Dependents
Profit & Loss analysis for complete system serving selected buyer |  | Model parameter | Row label only
NOTE: Heat revenue reflects ACTUAL buyer absorption, not theoretical module output |  | Pull actual heat buyer takes | Row label only
CONFIGURATION
Selected buyer profile |  | Pull selected buyer scenario | Pulls value from 5. Buyer Profile!B11
Modules in system |  | Pull system size | Pulls value from 5. Buyer Profile!B35 | 9. System P&L!B17 - TOTAL COMPUTE REVENUE (£/yr)
Chipset |  | Pull configuration for context | Pulls value from 0. Rack Profile!B6
Cooling method |  | Pull configuration for context | Pulls value from 0. Rack Profile!B17
COMPUTE REVENUE
Module IT capacity (kW) | From Module Criteria | Pull module size for revenue calc | Pulls value from 1. Module Criteria!B5 | 9. System P&L!B16 - Compute revenue per module (£/yr)
Rack rate (£/kW/month) | Input assumption - pulled from Module Criteria | Pull compute pricing assumption | Pulls value from 1. Module Criteria!B6 | 9. System P&L!B16 - Compute revenue per module (£/yr)
Operating hours/year | From selected process profile | Pull utilisation for revenue calc | Pulls value from 5. Buyer Profile!B18
Utilisation assumption (%) | Input assumption - pulled from Module Criteria | Pull capacity utilisation rate | Pulls value from 1. Module Criteria!B7 | 9. System P&L!B16 - Compute revenue per module (£/yr)
Compute revenue per module (£/yr) | Racks × rate × 12 months × utilisation | Calculate single module compute income | Calculated from upstream values for Compute revenue per module (£/yr) | 9. System P&L!B17 - TOTAL COMPUTE REVENUE (£/yr)
TOTAL COMPUTE REVENUE (£/yr) | Per module × number of modules | Calculate all modules compute income | Calculated from upstream values for TOTAL COMPUTE REVENUE (£/yr) | 9. System P&L!B33 - Compute revenue (£/yr)
HEAT REVENUE
Heat price (£/MWh) | Input assumption - pulled from Module Criteria | Pull heat sales pricing | Pulls value from 1. Module Criteria!B29 | 9. System P&L!B24 - Theoretical heat revenue (£/yr); 9. System P&L!B27 - ACTUAL HEAT REVENUE (£/yr)
Buyer operating hours/year | Hours buyer process runs annually | Pull utilisation for revenue calc | Pulls value from 5. Buyer Profile!B18 | 9. System P&L!B24 - Theoretical heat revenue (£/yr); 9. System P&L!B27 - ACTUAL HEAT REVENUE (£/yr)
Theoretical heat output (kWth) | Total system thermal generation capacity | Calculate max heat sales potential | Pulls value from 5. Buyer Profile!B46 | 9. System P&L!B24 - Theoretical heat revenue (£/yr); 9. System P&L!B29 - Heat utilisation (%)
Theoretical heat revenue (£/yr) | kWth × hours ÷ 1000 × £/MWh = £ (if buyer absorbed all) | Calculate max heat income potential | Calculated from upstream values for Theoretical heat revenue (£/yr) | 9. System P&L!B30 - Lost heat revenue (£/yr)
Actual buyer absorption (kWth) | Limited by buyer heat demand | Pull actual heat buyer takes | Pulls value from 5. Buyer Profile!B47 | 9. System P&L!B27 - ACTUAL HEAT REVENUE (£/yr); 9. System P&L!B29 - Heat utilisation (%)
ACTUAL HEAT REVENUE (£/yr) | kWth × hours ÷ 1000 × £/MWh = £ | Calculate realised heat income | Calculated from upstream values for ACTUAL HEAT REVENUE (£/yr) | 9. System P&L!B30 - Lost heat revenue (£/yr); 9. System P&L!B34 - Heat revenue (£/yr)
Heat utilisation (%) | Actual absorption ÷ theoretical output | Measure heat sales efficiency | Conditional logic for Heat utilisation (%) | 9. System P&L!B53 - Heat utilisation efficiency (%)
Lost heat revenue (£/yr) | Foregone income from excess heat - key efficiency metric | Quantify revenue lost to rejection | Calculated from upstream values for Lost heat revenue (£/yr) | 9. System P&L!B54 - Revenue lost to heat rejection (£/y...
TOTAL REVENUE
Compute revenue (£/yr) |  | Financial input or calculation | Formula: Compute revenue (£/yr) | 9. System P&L!B35 - TOTAL REVENUE (£/yr)
Heat revenue (£/yr) |  | Financial input or calculation | Formula: Heat revenue (£/yr) | 9. System P&L!B35 - TOTAL REVENUE (£/yr); 9. System P&L!B36 - Heat as % of total revenue
TOTAL REVENUE (£/yr) |  | Sum all revenue streams | Calculated from upstream values for TOTAL REVENUE (£/yr) | 9. System P&L!B36 - Heat as % of total revenue; 9. System P&L!B45 - Gross profit (£/yr); 9. System P&L!B46 - Gross margin (%)
Heat as % of total revenue | Contribution of heat sales to total revenue | Sum all revenue streams | Conditional logic for Heat as % of total revenue
OPERATING COSTS
Base system opex (£/yr) | Module opex + shared overhead (excl. rejection) | Pull core operating costs | Pulls value from 7. System Opex!B23
Heat rejection opex (£/yr) | Cost to reject excess heat | Pull rejection operating costs | Pulls value from 7. System Opex!B28 | 9. System P&L!B55 - Cost of heat rejection (£/yr)
Hydraulic augmentation opex (£/yr) |  | Pull pump operating costs | Pulls value from 7. System Opex!B35
TOTAL OPEX (£/yr) |  | Sum all operating costs | Pulls value from 7. System Opex!B37 | 9. System P&L!B45 - Gross profit (£/yr)
PROFIT & RETURNS
Gross profit (£/yr) | Total revenue - Total opex | Calculate operating profit | Calculated from upstream values for Gross profit (£/yr) | 9. System P&L!B46 - Gross margin (%); 9. System P&L!B49 - Simple payback (years); 9. System P&L!B50 - Unlevered ROI (%); 9. System P&L!B57 - Heat inefficiency as % of potential...
Gross margin (%) | Gross profit ÷ Total revenue | Calculate profit percentage | Conditional logic for Gross margin (%)
Total system capex (£) |  | Pull investment requirement | Pulls value from 6. System Capex!B46 | 9. System P&L!B49 - Simple payback (years); 9. System P&L!B50 - Unlevered ROI (%)
Simple payback (years) | Capex ÷ Annual profit (ignores time value of money) | Calculate investment recovery time | Conditional logic for Simple payback (years)
Unlevered ROI (%) | Annual profit ÷ Capex | Calculate return on investment | Conditional logic for Unlevered ROI (%)
EFFICIENCY METRICS
Heat utilisation efficiency (%) | Proportion of generated heat actually sold | Measure heat sales efficiency | Formula: Heat utilisation efficiency (%)
Revenue lost to heat rejection (£/yr) | Foregone heat revenue due to oversizing | Quantify rejection revenue impact | Formula: Revenue lost to heat rejection (£/yr) | 9. System P&L!B56 - Total heat inefficiency cost (£/yr)
Cost of heat rejection (£/yr) | Opex to reject unsold heat | Quantify rejection cost impact | Formula: Cost of heat rejection (£/yr) | 9. System P&L!B56 - Total heat inefficiency cost (£/yr)
Total heat inefficiency cost (£/yr) | Lost revenue + rejection cost = true cost of thermal mismatch | Sum heat-related losses | Calculated from upstream values for Total heat inefficiency cost (£/yr) | 9. System P&L!B57 - Heat inefficiency as % of potential...
Heat inefficiency as % of potential profit | Shows how much profit is eroded by thermal mismatch | Show heat loss as share of potential | Conditional logic for Heat inefficiency as % of potential profit

## 11. Reference Data
REFERENCE DATA |  |  |  |  | Intent | Explanation | Dependents
Lookup tables and assumptions used throughout the model |  |  |  |  | Model parameter | Row label only
Yellow cells are adjustable inputs |  |  |  |  | Model parameter | Row label only
HEAT REJECTION INFRASTRUCTURE
Equipment selection based on total system thermal output (worst-case sizing) |  |  |  |  | Reference cost for thermal equipment | Row label only
Operating costs based on actual excess heat rejected |  |  |  |  | Financial input or calculation | Row label only
Method | Capacity Range | Capex (£/kWth) | Opex (£/kWth/yr) | Notes | Model parameter | Text value for Method
Dry cooler | <100 kWth | 150 | 70 | Air-cooled, no water consumption. Limited by ambient temp on hot days. | Reference cost for rejection equipment | Text value for Dry cooler
Adiabatic cooler | 100-499 kWth | 220 | 110 | Spray-assisted cooling. Higher capex, water consumption adds to opex. | Reference cost for rejection equipment | Text value for Adiabatic cooler
Cooling tower | ≥500 kWth | 180 | 95 | Evaporative cooling. Most efficient at scale, requires water treatment. | Reference cost for rejection equipment | Text value for Cooling tower
Capacity Thresholds |  |  |  |  | Reference decision boundary value | Row label only
Dry cooler max (kWth) | 100 |  |  |  | Reference cost for rejection equipment | Input parameter: Dry cooler max (kWth) | 5. Buyer Profile!B51 - Rejection method
Adiabatic cooler max (kWth) | 500 |  |  |  | Reference cost for rejection equipment | Input parameter: Adiabatic cooler max (kWth) | 5. Buyer Profile!B51 - Rejection method
COOLING METHOD CHARACTERISTICS
Performance and cost characteristics by liquid cooling approach |  |  |  |  | Financial input or calculation | Row label only
Cooling Method | Heat Capture | Capture Temp | Capex Premium | Source ΔT (°C) | Model parameter | Text value for Cooling Method
Direct-to-Chip (DTC) | 75% | 57.5°C | +15% | 10 | Model parameter | Text value for Direct-to-Chip (DTC)
Single-Phase Immersion | 95% | 50°C | +25% | 6 | Reference cost for immersion equipment | Text value for Single-Phase Immersion
Two-Phase Immersion | 98% | 55°C | +40% | 3 | Reference cost for immersion equipment | Text value for Two-Phase Immersion
Rear Door Heat Exchanger | 50% | 45°C | +10% | 12 | Reference cost for thermal equipment | Text value for Rear Door Heat Exchanger
Air Cooled (Reference) | 5% | 35°C | 0% | 15 | Model parameter | Text value for Air Cooled (Reference)
CHIPSET SPECIFICATIONS
GPU specifications by model |  |  |  |  | Model parameter | Row label only
Chipset | TDP (W) | Chips/Server | T_junction (°C) | Notes | Model parameter | Text value for Chipset
NVIDIA H100 | 700 | 8 | 83 | Current gen. DTC reference design available. | Reference specs for NVIDIA H100 | Section header
NVIDIA H200 | 700 | 8 | 83 | H100 + HBM3e memory upgrade. Same thermal. | Reference specs for NVIDIA H200 | Section header
NVIDIA B200 | 1000 | 8 | 85 | Blackwell. Higher TDP, higher capture temps expected. | Reference specs for NVIDIA B200 | Section header
AMD MI300X | 750 | 8 | 90 | Instinct series. Competitive with H100. | Reference specs for AMD MI300X | Section header
Intel Gaudi 3 | 600 | 8 | 95 | AI accelerator. Lower TDP. | Model parameter | Input parameter: Intel Gaudi 3
HEAT PUMP ECONOMICS
COP and operating cost by temperature lift |  |  |  |  | Reference heat pump efficiency parameters | Row label only
Target delivery temp (°C) | 75 | Reference COPs at this delivery temp (using η from row 110) |  |  | Temperature parameter for thermal design | Input parameter: Target delivery temp (°C) | 11. Reference Data!B47 - 57.5; 11. Reference Data!C47 - 57.5; 11. Reference Data!B48 - 50; 11. Reference Data!C48 - 50; 11. Reference Data!B49 - 55; 11. Reference Data!C49 - 55; 11. Reference Data!B50 - 45; 11. Reference Data!C50 - 45
Source Temp (°C) | Lift (°C) | Est. COP | kWe per kWth | Cooling Method | Temperature parameter for thermal design | Text value for Source Temp (°C)
57.5 |  |  |  | DTC | Model parameter | Calculated from upstream values for 57.5 | 11. Reference Data!C47 - 57.5
50 |  |  |  | Single-Phase Immersion | Model parameter | Calculated from upstream values for 50 | 11. Reference Data!C48 - 50
55 |  |  |  | Two-Phase Immersion | Model parameter | Calculated from upstream values for 55 | 11. Reference Data!C49 - 55
45 |  |  |  | RDHX | Model parameter | Calculated from upstream values for 45 | 11. Reference Data!C50 - 45
PROCESS ΔT REFERENCE
Temperature differential by industrial process (affects flow requirements) |  |  |  |  | Temperature parameter for thermal design | Row label only
Process | Typical ΔT (°C) | Constraint Type | Source |  | Model parameter | Text value for Process
Pasteurisation | 5 | Flow-constrained | Tetra Pak |  | Model parameter | Input parameter: Pasteurisation
Swimming pools | 5 | Flow-constrained | Kensa |  | Model parameter | Input parameter: Swimming pools
Building HVAC | 10 | Balanced | ASHRAE 90.1 |  | Model parameter | Input parameter: Building HVAC
CIP systems | 12 | Balanced | CSI Designs |  | Model parameter | Input parameter: CIP systems
Commercial laundry | 18 | Thermal-constrained | AERCO |  | Model parameter | Input parameter: Commercial laundry
District heating | 30 | Thermal-constrained | CIBSE CP1 |  | Model parameter | Input parameter: District heating
MODULE HARDWARE CAPEX
Itemised costs for module components - yellow cells are adjustable inputs |  |  |  |  | Financial input or calculation | Row label only
Component | Cost (£) | Unit | Scaling Basis | Source | Model parameter | Text value for Component
ENCLOSURE & STRUCTURE | [5 empty] | Row label only
Container shell (40ft) | 35000 | per module | Fixed | Industry average | Reference cost for enclosure | Input assumption: Container shell (40ft) | 2. Module Capex!B13 - Container shell
Container fit-out (electrical, HVAC prep) | 25000 | per module | Fixed | Industry average | Reference cost for enclosure | Input assumption: Container fit-out (electrical, HVAC prep) | 2. Module Capex!B14 - Container fit-out
Rack enclosure (42U enclosed) | 2000 | per rack | Rack count | CDW/RackSolutions | Reference cost per rack | Input assumption: Rack enclosure (42U enclosed) | 2. Module Capex!B15 - Rack enclosures; 2. Module Capex!C15 - Rack enclosures
DTC COOLING COMPONENTS | [5 empty] | Row label only
Cold plate kit (per server) | 250 | per server | Server count | CoolIT/Asetek | Reference cost for DTC equipment | Input parameter: Cold plate kit (per server) | 2. Module Capex!B19 - Cold plate kits
CDU (Coolant Distribution Unit) | 35000 | per module | Fixed base | Vertiv/Schneider | Reference cost for DTC equipment | Input assumption: CDU (Coolant Distribution Unit) | 2. Module Capex!B20 - CDU (base)
CDU capacity scaling | 80 | per kW | Module IT kW | Industry estimate | Reference cost for DTC equipment | Input parameter: CDU capacity scaling | 2. Module Capex!B21 - CDU (capacity scaling)
Manifolds & quick-connects | 150 | per server | Server count | Industry estimate | Reference cost for DTC equipment | Input parameter: Manifolds & quick-connects | 2. Module Capex!B22 - Manifolds & quick-connects
Primary loop piping | 5000 | per module | Fixed | Industry estimate | Model parameter | Input assumption: Primary loop piping | 2. Module Capex!B23 - Primary loop piping
IMMERSION COOLING COMPONENTS | [5 empty] | Row label only
Single-phase immersion tank | 28000 | per rack | Rack count | GRC/LiquidCool | Reference cost for immersion equipment | Input assumption: Single-phase immersion tank | 2. Module Capex!B27 - Immersion tanks
Two-phase immersion tank | 45000 | per rack | Rack count | LiquidStack/Asperitas | Reference cost for immersion equipment | Input assumption: Two-phase immersion tank | 2. Module Capex!B27 - Immersion tanks
Dielectric fluid - single-phase | 12 | per litre | Tank volume | Shell/Cargill | Reference cost for immersion equipment | Input parameter: Dielectric fluid - single-phase | 2. Module Capex!B28 - Dielectric fluid (initial fill)
Dielectric fluid - two-phase | 120 | per litre | Tank volume | 3M Novec | Reference cost for immersion equipment | Input parameter: Dielectric fluid - two-phase | 2. Module Capex!B28 - Dielectric fluid (initial fill)
Fluid volume per rack (single-phase) | 600 | litres | Per rack | Industry average | Reference cost per rack | Input parameter: Fluid volume per rack (single-phase) | 2. Module Capex!B28 - Dielectric fluid (initial fill)
Fluid volume per rack (two-phase) | 400 | litres | Per rack | Industry average | Reference cost per rack | Input parameter: Fluid volume per rack (two-phase) | 2. Module Capex!B28 - Dielectric fluid (initial fill)
Fluid management system | 15000 | per module | Fixed | Industry estimate | Reference fluid cost or volume | Input assumption: Fluid management system | 2. Module Capex!B29 - Fluid management system
POWER DISTRIBUTION | [5 empty] | Row label only
High-density PDU (per rack) | 3000 | per rack | Rack count | Vertiv/Raritan | Reference cost per rack | Input assumption: High-density PDU (per rack) | 2. Module Capex!B33 - Rack PDUs
Module power distribution | 180 | per kW | Module IT kW | Schneider Electric | Reference cost for electrical equipment | Input parameter: Module power distribution | 2. Module Capex!B34 - Module power distribution
Electrical panels & switchgear | 20000 | per module | Fixed | Industry estimate | Reference cost for electrical equipment | Input assumption: Electrical panels & switchgear | 2. Module Capex!B35 - Electrical panels & switchgear
THERMAL INTEGRATION | [5 empty] | Row label only
Primary heat exchanger | 12000 | per module | Fixed base | Alfa Laval/SWEP | Reference cost for thermal equipment | Input assumption: Primary heat exchanger | 2. Module Capex!B39 - Primary heat exchanger (base)
Heat exchanger scaling | 25 | per kW | Module thermal kW | Industry estimate | Reference cost for thermal equipment | Input parameter: Heat exchanger scaling | 2. Module Capex!B40 - Heat exchanger (capacity scaling)
Thermal integration skid (pumps, valves) | 18000 | per module | Fixed | Industry estimate | Reference cost for thermal equipment | Input assumption: Thermal integration skid (pumps, valves) | 2. Module Capex!B41 - Thermal integration skid
Instrumentation & sensors | 8000 | per module | Fixed | Industry estimate | Reference cost for monitoring equipment | Input assumption: Instrumentation & sensors | 2. Module Capex!B42 - Instrumentation & sensors
MONITORING & CONTROLS | [5 empty] | Row label only
BMS base system | 18000 | per module | Fixed | Schneider/Honeywell | Reference cost for monitoring equipment | Input assumption: BMS base system | 2. Module Capex!B46 - BMS base system
Per-rack monitoring | 500 | per rack | Rack count | Industry estimate | Reference cost per rack | Input parameter: Per-rack monitoring | 2. Module Capex!B47 - Per-rack monitoring
Network infrastructure | 8000 | per module | Fixed | Industry estimate | Reference cost for network equipment | Input assumption: Network infrastructure | 2. Module Capex!B48 - Network infrastructure
HEAT PUMP EFFICIENCY MODEL
Carnot-based COP model with configurable efficiency factor |  |  |  |  | Reference heat pump efficiency parameters | Row label only
Carnot efficiency factor (η) | 0.45 | Conservative default (range: 0.40-0.55 per NREL) |  |  | Reference heat pump efficiency parameters | Input parameter: Carnot efficiency factor (η) | 0. Rack Profile!B52 - Estimated COP at recommended output; 0. Rack Profile!B61 - COP at this lift; 1. Module Criteria!B17 - Heat pump COP; 11. Reference Data!C47 - 57.5; 11. Reference Data!C48 - 50; 11. Reference Data!C49 - 55; 11. Reference Data!C50 - 45
Minimum practical COP | 2 | Floor to prevent unrealistic values |  |  | Reference heat pump efficiency parameters | Input parameter: Minimum practical COP | 0. Rack Profile!B52 - Estimated COP at recommended output; 0. Rack Profile!B61 - COP at this lift; 1. Module Criteria!B17 - Heat pump COP
Maximum practical COP | 8 | Ceiling to prevent unrealistic values |  |  | Reference heat pump efficiency parameters | Input parameter: Maximum practical COP | 0. Rack Profile!B52 - Estimated COP at recommended output; 0. Rack Profile!B61 - COP at this lift; 1. Module Criteria!B17 - Heat pump COP
Formula: COP = η × T_hot(K) / (T_hot - T_cold) |  |  |  |  | Reference heat pump efficiency parameters | Row label only
Where T in Kelvin = T in °C + 273.15 |  |  |  |  | Model parameter | Row label only
HYDRAULIC AUGMENTATION RATES
For flow deficit handling when buyer flow > module flow |  |  |  |  | Fluid flow parameter for hydraulic design | Row label only
Augmentation pump capex (£ per m³/hr) | 150 | Centrifugal pump sized for flow deficit |  |  | Reference pump specifications or cost | Input parameter: Augmentation pump capex (£ per m³/hr) | 6. System Capex!B37 - Augmentation pump capex
Augmentation pump power (kW per m³/hr) | 0.1 | At ~25m head typical for HVAC systems |  |  | Reference cost for electrical equipment | Input parameter: Augmentation pump power (kW per m³/hr) | 5. Buyer Profile!B83 - Augmentation pump power (kW)
Mixing valve + controls (£) | 2500 | 3-way valve with actuator and controller |  |  | Reference hydraulic equipment cost | Input assumption: Mixing valve + controls (£) | 6. System Capex!B38 - Mixing valve + controls
Pipe upsizing allowance (£ per m³/hr) | 50 | Applied when flow deficit > 20 m³/hr |  |  | Reference hydraulic equipment cost | Input parameter: Pipe upsizing allowance (£ per m³/hr) | 6. System Capex!B39 - Pipe upsizing allowance
Standard augmentation pump capacity (m³/hr) | 25 | Typical centrifugal pump rating for HVAC |  |  | Reference pump specifications or cost | Input parameter: Standard augmentation pump capacity (m³/hr) | 5. Buyer Profile!B84 - Augmentation pumps required; 5. Buyer Profile!B85 - Augmentation pump capacity (m³/hr); 6. System Capex!B37 - Augmentation pump capex

## 12. Process Library
PROCESS LIBRARY
Reference data for industrial heat demand profiles
Process | Size | Temp (°C) | Load (kWth) | Hrs/yr | Notes | Dropdown Name | Source | ΔT (°C) | Source URL
Pasteurisation | Small | 72 | 65 | 4000 | Craft dairy/microbrewery (5,000 L/day) | Pasteurisation - Small | Tetra Pak Dairy Processing Handbook | 5 | https://dairyprocessinghandbook.tetrapak.com/chapter/heat-exchangers
Pasteurisation | Medium | 72 | 500 | 5500 | Regional dairy (50,000 L/day) | Pasteurisation - Medium | Tetra Pak Dairy Processing Handbook | 5 | https://dairyprocessinghandbook.tetrapak.com/chapter/heat-exchangers
Pasteurisation | Large | 72 | 2500 | 7000 | Industrial dairy (250,000+ L/day) | Pasteurisation - Large | Tetra Pak Dairy Processing Handbook | 5 | https://dairyprocessinghandbook.tetrapak.com/chapter/heat-exchangers
CIP (Clean-in-Place) | Small | 85 | 50 | 3000 | Single vessel/tank system | CIP (Clean-in-Place) - Small | CSI Designs - Heat Exchangers in CIP | 12 | https://www.csidesigns.com/blog/articles/how-heat-exchangers-work-during-clean-in-place
CIP (Clean-in-Place) | Medium | 85 | 150 | 4000 | Multi-tank dairy/brewery | CIP (Clean-in-Place) - Medium | CSI Designs - Heat Exchangers in CIP | 12 | https://www.csidesigns.com/blog/articles/how-heat-exchangers-work-during-clean-in-place
CIP (Clean-in-Place) | Large | 85 | 400 | 5000 | Full processing plant | CIP (Clean-in-Place) - Large | CSI Designs - Heat Exchangers in CIP | 12 | https://www.csidesigns.com/blog/articles/how-heat-exchangers-work-during-clean-in-place
Bottle washing | Small | 80 | 35 | 4000 | Craft bottling line | Bottle washing - Small | GEA Brewing Systems | 10 | https://www.gea.com/en/products/brewery-systems
Bottle washing | Medium | 80 | 120 | 5500 | Regional bottler (10k bottles/hr) | Bottle washing - Medium | GEA Brewing Systems | 10 | https://www.gea.com/en/products/brewery-systems
Bottle washing | Large | 80 | 280 | 7000 | Industrial (50k+ bottles/hr) | Bottle washing - Large | GEA Brewing Systems | 10 | https://www.gea.com/en/products/brewery-systems
Parts degreasing | Small | 60 | 25 | 3000 | Workshop/small batch | Parts degreasing - Small | Dürr Systems AG | 15 | https://www.durr.com/en/products-and-services/cleaning-technology
Parts degreasing | Medium | 60 | 75 | 4500 | Automotive supplier | Parts degreasing - Medium | Dürr Systems AG | 15 | https://www.durr.com/en/products-and-services/cleaning-technology
Parts degreasing | Large | 60 | 180 | 6000 | Heavy manufacturing | Parts degreasing - Large | Dürr Systems AG | 15 | https://www.durr.com/en/products-and-services/cleaning-technology
Commercial laundry | Small | 70 | 130 | 4000 | Hotel (500 kg/day) | Commercial laundry - Small | AERCO Laundry Sizing Guide | 18 | https://www.aerco.com/dfsmedia/0533dbba17714b1ab581ab07a4cbb521/58930-source/sizing-laundry-hot-water-systems
Commercial laundry | Medium | 70 | 670 | 5500 | Hospital (2,500 kg/day) | Commercial laundry - Medium | AERCO Laundry Sizing Guide | 18 | https://www.aerco.com/dfsmedia/0533dbba17714b1ab581ab07a4cbb521/58930-source/sizing-laundry-hot-water-systems
Commercial laundry | Large | 70 | 2700 | 7000 | Industrial (10,000+ kg/day) | Commercial laundry - Large | AERCO Laundry Sizing Guide | 18 | https://www.aerco.com/dfsmedia/0533dbba17714b1ab581ab07a4cbb521/58930-source/sizing-laundry-hot-water-systems
Timber drying | Small | 70 | 50 | 5000 | Joinery/furniture (5m³) | Timber drying - Small | Oklahoma State Extension - Kiln Drying | 18 | https://extension.okstate.edu/fact-sheets/fundamental-aspects-of-kiln-drying-lumber.html
Timber drying | Medium | 70 | 200 | 6000 | Small sawmill (25m³) | Timber drying - Medium | Oklahoma State Extension - Kiln Drying | 18 | https://extension.okstate.edu/fact-sheets/fundamental-aspects-of-kiln-drying-lumber.html
Timber drying | Large | 70 | 500 | 7000 | Industrial kiln (100m³) | Timber drying - Large | Oklahoma State Extension - Kiln Drying | 18 | https://extension.okstate.edu/fact-sheets/fundamental-aspects-of-kiln-drying-lumber.html
Paint curing | Small | 80 | 50 | 3000 | Small paint shop | Paint curing - Small | Dürr Paint Systems | 15 | https://www.durr.com/en/products-and-services/paint-systems
Paint curing | Medium | 80 | 150 | 4500 | Automotive components | Paint curing - Medium | Dürr Paint Systems | 15 | https://www.durr.com/en/products-and-services/paint-systems
Paint curing | Large | 80 | 350 | 6000 | OEM paint line | Paint curing - Large | Dürr Paint Systems | 15 | https://www.durr.com/en/products-and-services/paint-systems
Textile drying | Small | 90 | 60 | 4000 | Small finishing mill | Textile drying - Small | Monforts Textilmaschinen | 20 | https://www.monforts.de/en/
Textile drying | Medium | 90 | 200 | 5500 | Regional mill | Textile drying - Medium | Monforts Textilmaschinen | 20 | https://www.monforts.de/en/
Textile drying | Large | 90 | 450 | 7000 | Industrial stenter line | Textile drying - Large | Monforts Textilmaschinen | 20 | https://www.monforts.de/en/
District heating | Small | 70 | 500 | 4500 | 100-200 homes | District heating - Small | CIBSE CP1 Heat Networks Code of Practice | 30 | https://www.cibsejournal.com/technical/the-perfect-return-heat-network-return-temperatures/
District heating | Medium | 70 | 2000 | 5000 | 400-800 homes | District heating - Medium | CIBSE CP1 Heat Networks Code of Practice | 30 | https://www.cibsejournal.com/technical/the-perfect-return-heat-network-return-temperatures/
District heating | Large | 70 | 5000 | 5500 | 1,000+ homes | District heating - Large | CIBSE CP1 Heat Networks Code of Practice | 30 | https://www.cibsejournal.com/technical/the-perfect-return-heat-network-return-temperatures/
Building HVAC | Small | 60 | 80 | 3500 | Small office (1,000m²) | Building HVAC - Small | ASHRAE 90.1 / CIBSE Guide B | 12 | https://www.trane.com/content/dam/Trane/Commercial/global/products-systems/education-training/engineers-newsletters/standards-codes/ADM-APN070-EN_06032019.pdf
Building HVAC | Medium | 60 | 300 | 4000 | Large office (5,000m²) | Building HVAC - Medium | ASHRAE 90.1 / CIBSE Guide B | 12 | https://www.trane.com/content/dam/Trane/Commercial/global/products-systems/education-training/engineers-newsletters/standards-codes/ADM-APN070-EN_06032019.pdf
Building HVAC | Large | 60 | 1000 | 4500 | Campus/hospital | Building HVAC - Large | ASHRAE 90.1 / CIBSE Guide B | 12 | https://www.trane.com/content/dam/Trane/Commercial/global/products-systems/education-training/engineers-newsletters/standards-codes/ADM-APN070-EN_06032019.pdf
Swimming pool | Small | 30 | 60 | 6000 | Hotel pool (12x6m) | Swimming pool - Small | Kensa Heat Pumps - Pools Application Guide | 5 | https://www.kensaheatpumps.com/wp-content/uploads/2014/09/AIS—Heat-pumps-and-swimming-pools-—2.0_with_metadata.pdf
Swimming pool | Medium | 30 | 180 | 7000 | Leisure centre (25m) | Swimming pool - Medium | Kensa Heat Pumps - Pools Application Guide | 5 | https://www.kensaheatpumps.com/wp-content/uploads/2014/09/AIS—Heat-pumps-and-swimming-pools-—2.0_with_metadata.pdf
Swimming pool | Large | 30 | 450 | 8000 | Competition (50m) | Swimming pool - Large | Kensa Heat Pumps - Pools Application Guide | 5 | https://www.kensaheatpumps.com/wp-content/uploads/2014/09/AIS—Heat-pumps-and-swimming-pools-—2.0_with_metadata.pdf
Glasshouse heating | Small | 50 | 200 | 3500 | 1 hectare tomatoes | Glasshouse heating - Small | Dutch Greenhouses / AHDB Horticulture | 20 | https://dutchgreenhouses.com/en/climate/heating
Glasshouse heating | Medium | 50 | 750 | 4000 | 4 hectares mixed | Glasshouse heating - Medium | Dutch Greenhouses / AHDB Horticulture | 20 | https://dutchgreenhouses.com/en/climate/heating
Glasshouse heating | Large | 50 | 2000 | 4500 | 10+ hectares | Glasshouse heating - Large | Dutch Greenhouses / AHDB Horticulture | 20 | https://dutchgreenhouses.com/en/climate/heating
Reactor heating | Small | 90 | 60 | 5000 | Pilot/R&D reactor | Reactor heating - Small | IChemE Process Data | 10 | https://www.icheme.org/
Reactor heating | Medium | 90 | 200 | 6000 | Batch chemical | Reactor heating - Medium | IChemE Process Data | 10 | https://www.icheme.org/
Reactor heating | Large | 90 | 450 | 7000 | Continuous process | Reactor heating - Large | IChemE Process Data | 10 | https://www.icheme.org/
Fermentation | Small | 35 | 25 | 6000 | Craft brewery (5k hl/yr) | Fermentation - Small | Clarke Energy / Brewery Best Practice | 5 | https://www.clarke-energy.com/applications/breweries/
Fermentation | Medium | 35 | 100 | 7000 | Regional (50k hl/yr) | Fermentation - Medium | Clarke Energy / Brewery Best Practice | 5 | https://www.clarke-energy.com/applications/breweries/
Fermentation | Large | 35 | 280 | 8000 | Industrial biotech | Fermentation - Large | Clarke Energy / Brewery Best Practice | 5 | https://www.clarke-energy.com/applications/breweries/
MODULE MATCHING SUMMARY
Single 250kWth module best matches:
• Pasteurisation - Small/Medium
• CIP - All sizes
• Bottle washing - All sizes
• Parts degreasing - All sizes
• Commercial laundry - Small
• Timber drying - Small/Medium
• Paint curing - All sizes
• Textile drying - Small/Medium
• Building HVAC - Small/Medium
• Swimming pool - All sizes
• Glasshouse heating - Small
• Reactor heating - Small/Medium
• Fermentation - All sizes
SOURCE REFERENCES
AHDB Horticulture | UK Agriculture & Horticulture Development Board - Glasshouse energy benchmarks
Alfa Laval CIP Systems | Industrial CIP system specifications and energy requirements
ΔT SOURCE REFERENCES | Timber drying technology handbook
CIBSE Guide A/B | UK Chartered Institution of Building Services Engineers design guides
Process Type | ΔT (°C) | Source | URL
Pasteurisation | 5 | Tetra Pak Dairy Processing Handbook | https://dairyprocessinghandbook.tetrapak.com/chapter/heat-exchangers
CIP (Clean-in-Place) | 12 | CSI Designs - Heat Exchangers in CIP | https://www.csidesigns.com/blog/articles/how-heat-exchangers-work-during-clean-in-place
Bottle washing | 10 | GEA Brewing Systems | https://www.gea.com/en/products/brewery-systems
Parts degreasing | 15 | Dürr Systems AG | https://www.durr.com/en/products-and-services/cleaning-technology
Commercial laundry | 18 | AERCO Laundry Sizing Guide | https://www.aerco.com/dfsmedia/0533dbba17714b1ab581ab07a4cbb521/58930-source/sizing-laundry-hot-water-systems
Timber drying | 18 | Oklahoma State Extension - Kiln Drying | https://extension.okstate.edu/fact-sheets/fundamental-aspects-of-kiln-drying-lumber.html
Paint curing | 15 | Dürr Paint Systems | https://www.durr.com/en/products-and-services/paint-systems
Textile drying | 20 | Monforts Textilmaschinen | https://www.monforts.de/en/
District heating | 30 | CIBSE CP1 Heat Networks Code of Practice | https://www.cibsejournal.com/technical/the-perfect-return-heat-network-return-temperatures/
Building HVAC | 12 | ASHRAE 90.1 / CIBSE Guide B | https://www.trane.com/content/dam/Trane/Commercial/global/products-systems/education-training/engineers-newsletters/standards-codes/ADM-APN070-EN_06032019.pdf
Swimming pool | 5 | Kensa Heat Pumps - Pools Application Guide | https://www.kensaheatpumps.com/wp-content/uploads/2014/09/AIS—Heat-pumps-and-swimming-pools-—2.0_with_metadata.pdf
Glasshouse heating | 20 | Dutch Greenhouses / AHDB Horticulture | https://dutchgreenhouses.com/en/climate/heating
Reactor heating | 10 | IChemE Process Data | https://www.icheme.org/
Fermentation | 5 | Clarke Energy / Brewery Best Practice | https://www.clarke-energy.com/applications/breweries/
NOTES ON ΔT VALUES
• ΔT = temperature difference between supply and return water in the process heat loop
• Lower ΔT (5°C) = tight temperature control required, higher flow rate needed
• Higher ΔT (30°C) = wider temperature tolerance, lower flow rate acceptable
• Flow rate (m³/hr) = Thermal load (kW) / (4.18 × ΔT) × 3.6
• A process with ΔT=5°C needs 6× the flow rate of one with ΔT=30°C for same thermal load